## Slide 1
Assessing and Optimizing the Performance of
R-290 Integral Display Case

## Slide 2
Contents
2
Introduction
1
Objectives
2
3
4
5
6
System Description
Data Analysis
Preliminary Simulations
Inquiries

## Slide 3
Introduction
1

## Slide 4
Mission
4
Assessing and optimizing the performance of the following R-290 integral display case.
The system comprises:
  1 evaporator with 3 circuits of R290.
  3 Copeland Scroll ZB09KAU-TFD compressors.
  3 Danfoss D22-20 Micro-plate condensers.

## Slide 5
Mission
5
Design point/working conditions:
  Evaporation temperature: – 6 °C
  Cooling capacity per compressor/circuit: 2.5 kW
  Condensing temperature: 40 °C
  Subcooling: 1 K
  Superheat: 7 K to 10 K
  Number of circuits: 3
  Mass flow R-290 per circuit: 9.20 g/s
  Tair,out: – 2 °C
  Tair,in: 6 °C with 50% RH

## Slide 6
Objectives
2

## Slide 7
7
The main objectives could be summarized next:
  To analyze the experimental data of the current system.
  To model the current system using IMST-ART simulation tool in order to assess the system performance.
  To optimize the whole system in order to reduce the refrigerant charge and pressure drop while maintain the display case dimensions.

## Slide 8
System Description
3

## Slide 9
Evaporator
9
The current evaporator has the following dimensions:

## Slide 10
Evaporator
10
Inlet circuit 1 (C1)
Inlet circuit 2 (C2)
Inlet circuit 3 (C3)
Refrigeration Circuits by IMST-ART
It has 3x 150g R290 circuits arranged as follows:

## Slide 11
Condenser
11
The specifications of one condenser are:

## Slide 12
Compressor
12
The specifications of one compressor are:

## Slide 13
Compressor
13
The power correlation:

## Slide 14
Compressor
14
The mass flow rate correlation:

## Slide 15
Evaporator Fans
15
The air flow is generated by 6 diagonal flow EC fans, model K1G-200 from EBM Papst running at 1400 rpm in the current arrangement.
The dimensions of one fan:

## Slide 16
Evaporator Fans
16
The head vs flow rate curves are as follows:

## Slide 17
Data Analysis
4

## Slide 18
18
The experimental data has been rearranged and evaluated with REFPRO for each test point (Total number of points= 17278) as seen in the following Figures:

## Slide 19
19

## Slide 20
20

## Slide 21
Preliminary Simulations
5

## Slide 22
STA Analysis
22
Firstly, we have analyzed each system component separately to check the consistency between the numerical results and catalog or design data.
Standalone condenser analysis:

## Slide 23
STA Analysis
23
Standalone condenser analysis (cont.):

## Slide 24
STA Analysis
24
Standalone condenser analysis (cont.):
Parameter | IMST-ART | Catalog Data
Refrigerant Area (m2) | 0.38083 | 0.38
Inlet Sat. Temperature (CO) | 45.932 | 44.71
Outlet Sat. Temperature (CO) | 45.911 | 44.71
Capacity (kW) | 2.5063 | 2.5
Fluid Volume (L) | 0.17639 | 0.189

## Slide 25
STA Analysis
25
Standalone evaporator analysis:

## Slide 26
STA Analysis
26
Standalone evaporator analysis (cont.):

## Slide 27
Real Cycle Analysis
27
Secondly, we have simulated the whole system on IMST-ART using the experimental data at specific point.

## Slide 28
Real Cycle Analysis
28
We have made a parametric study to estimate the actual refrigerant charge which gives the outlet condenser enthalpy at this point.

## Slide 29
Real Cycle Analysis
29

## Slide 30
Inquiries
6

## Slide 31
31
To obtain an accurate evaluation of the system, we need some further information.
Our main inquires are listed below:
From the experimental data we have assumed that the secondary fluid used in the condenser is 30% propylene glycol + 70% water. Could you please confirm this?
Please, we need more data about the liquid line. This will result to a better estimation of the refrigerant charge.
We have assumed that the internal two tube rows of the evaporator were removed. Could you please confirm that issue? Also, we need to know the fin thickness and type.
Information about the expansion valve used in the current system.

## Slide 32
32
Our main inquires are listed below (cont.):
Data about the air-side pressure drop.
Clarifying the required speed for evaporator fans, and the possibility of varying the fan speed.
Information regarding the oil capacity of the compressor, and the refrigerant solubility in oil.
Experimental data about the power consumed by the compressors.
Clarifying the actual refrigerant charge in the current system. Because from our preliminary simulations we have concluded that the charge is insufficient.

## Slide 33
33
Our main inquires are listed below (cont.):
One way for optimizing the system is to increase the flow rate of secondary fluid used by condensers. So, could you confirm us the possibility of applying this solution for the current system?
If it is available, could you provide us with the thickness of plate used in the condensers.

## Slide 34
Thanks for Your Attention
Notes: * And I´m I looking forward for your questions and inquiries.