## Slide 1
Status Review
29.01.2018

## Slide 2: Last week:
Finished most of the work on the EES modell
Water measuring
Testing with dry air

## Slide 3: Condensing water
Starttime | Stoptime | Mass water [kg] | Mass water [kg/day] | Cycle
13:00 | 16:00 | 8.888 | 71.10 | 03:00

## Slide 4: Evaporator change
Same dimensions but better heat transmission
8K Superheat not possible
  E-Valve fully open with 12K SH
  Higher mass flow rate
  Higher evaporating temperature
  Lower condensing temperature
  Calculated TCOND is lower than Twater,IN  bubbles in front of a pressure sensor can lead to a great loss in accuracy
Changed Superheat setting to 13K
  Similar performance like old evaporator
=> Because of better heat transmission the charge is not enough

## Slide 5
Evaporator Design Comparison
2.1
3.1
3.4
2.4
3.8fIN
2.9
2.12 OUT
3.5
2.5
IN 2.8
1.9
3.12 OUT
1.5
1.12 OUT
3.9
1.4
1.1
IN 1.8
1
2
3
4
16
5
6
7
8
9
10
11
12
13
14
15
modified LIDL design
Original LIDL design
2.1 IN
3.1 IN
3.4
2.4
3.8
2.9
2.12 OUT
3.5
2.5
2.8
1.9
3.12 OUT
1.5
1.12 OUT
3.9
1.4
1.1 IN
1.8
1
2
3
4
16
5
6
7
8
9
10
11
12
13
14
15

## Slide 6: To-Do:
Change coil connections
Make corrections for condensing temperature (pdisch)