## Slide 1: Work Progress
27.11.17

## Slide 2: Previous Meeting
Room air velocity
  Include schematic about situation before/without ceiling & clarify test numbers of each configuration
  Re-do smoke test + schematics w/ closed curtain & Open ceiling to validate fan speed setting
  Two tests to confirm (Temp+Humidity AND Smoke) tests
    25% fan speed – closed curtain – open ceiling
    25% fan speed – closed curtain – closed ceiling
Low-charge system
  Flush is definitely a must. Whatever it takes.  Remove 1 Condensor?
Data processing
  Small error to fix w/ time stamps
EES model
  Look at literature sent
  SB to send A/C unit EES model from JL/VT
  http://pdsim.sourceforge.net/index.html or other HP simulation model

## Slide 3: Last week:
Used the drive to run the compressor with a higher frequency to ensure better oil return  No effect
Removed 300g R407c from IDC500 /w Kristian
Installed new compressor in drive test rig, refilled 460g R410a
/w Romain
25pct fan power tests (open ceiling vs closed ceiling)
Further work on Pythonscript
  All version issues solved
  Now able to read and resample data
  Several plots

## Slide 4: Previous Testing (30pct)
Chart: 
Norm Max | 0.2 | 0.2
Norm Min | 0.1 | 0.1
AVE PosA | 0.28199 | 0.28199
AVE PosB | 0.34827 | 0.34827
AVE PosC | 0.050942 | 0.050942

## Slide 5: 25pct fan power with Open Ceiling
Chart: 
Norm Max | 0.2 | 0.2
Norm Min | 0.1 | 0.1
AVE PosA | 0.32883 | 0.32883
AVE PosB | 0.1613 | 0.1613
AVE PosC | 0.0029167 | 0.0029167

## Slide 6: 25pct fan power with Open Ceiling
29°C
17°C
29°C

## Slide 7: (49)Evaporator temperature with open ceiling

## Slide 8: 25pct fan power with closed Ceiling
Chart: 
Norm Max | 0.2 | 0.2
Norm Min | 0.1 | 0.1
AVE PosA | 0.29139 | 0.29139
AVE PosB | 0.1641 | 0.1641
AVE PosC | 0.0024833 | 0.0024833

## Slide 9: 25pct fan power with closed Ceiling
29°C
17°C
29°C

## Slide 10: (CC)Evaporator temperature with closed ceiling

## Slide 11: Conclusion
Closed Ceiling
  More laminar air flow
  Air velocity is a little lower
  Chamber regulates slower / more unstable
  Evaporating temperature isn’t falling  Higher Product temperature
Open Ceiling
  Chamber regulates better
  Product temperature is lower than previous tests
  Higher turbulence
  Continue testing with Open Ceiling and 25 pct fan power

## Slide 12: CAD-model of new evaporator

## Slide 13: Oil levels
Comp OFF
Comp ON
Delivery Oil Lvl

## Slide 14: Power: 3MAF vs HATCOL
Test # | Spec | Condensing Temp | Product Temp [°C] |  |  |  | COP compr | Qevap Qcond hevap in + Select massflow | Pcp,meas | Qevap,select0K | Pcp,sel | Qcond | xcd,out (mselect) | xcd,out (mselect) | xcd,out (mselect)
35.00 | t_75 30pct OC | 35.00 | 5.35 | 10.54 | 0.98 | 5.34 | 2.33 | 5.68 | 2.44 | 7.01 | 2.31 | 7.84 | 0.20 | 0.10 | 0.13
48.00 | t_75 27pct OC | 35.00 | 6.23 | 11.43 | 1.97 | 6.02 | 2.27 | 5.76 | 2.54 | 8.07 | 2.26 | 8.12 | 0.27 | 0.21 | 0.25
AVG MAX MIN MED

## Slide 15: To do: