## Evap_Exp_V2
Test 24 Air-side Results: Evap_Exp_V2
Vact | 1811.6284 | kg/h
Vstd | 1875.6 | kg/h
∆P_Evap | 34.0652 | Pa
k (Evaporator Fan/Pump Duct Pressure Loss Coefficient) | 31.6472 | Pa.S2/kg.m3
∆P_Duct | 9.6835 | Pa
Actual Air Density @ Tair_in for Evap. | 1.2424 | kg/m3
Standard Air Density (Rho_std) | 1.2 | kg/m3
Actual Air Density @ Tair_out for Evap. | 1.2775 | kg/m3
Face Area (m2) | 0.34 | m2
ACT_SystemCurve (Evap_Exp_V2)
Vact (m3/h) | mact (kg/s) | uact (m/s) | ∆P_Evap_Act (pa) | ∆P_Duct_Act (pa) | ∆P_Tot_Act (Pa) | Vact/fan (m3/h)
2400 | 0.82825 | 1.9608 | 59.7853 | 16.9944 | 76.7798 | 400
2200 | 0.75923 | 1.7974 | 50.2363 | 14.2801 | 64.5163 | 366.6667
2000 | 0.69021 | 1.634 | 41.5176 | 11.8017 | 53.3193 | 333.3333
1811.6284 | 0.6252 | 1.4801 | 34.0652 | 9.6833 | 43.7484 | 301.9381
1800 | 0.62119 | 1.4706 | 33.6292 | 9.5594 | 43.1886 | 300
1600 | 0.55217 | 1.3072 | 26.5713 | 7.5531 | 34.1243 | 266.6667
1400 | 0.48315 | 1.1438 | 20.3436 | 5.7828 | 26.1265 | 233.3333
1200 | 0.41413 | 0.98039 | 14.9463 | 4.2486 | 19.1949 | 200
1000 | 0.3451 | 0.81699 | 10.3794 | 2.9504 | 13.3298 | 166.6667
800 | 0.27608 | 0.65359 | 6.6428 | 1.8883 | 8.5311 | 133.3333
600 | 0.20706 | 0.4902 | 3.7366 | 1.0622 | 4.7987 | 100
400 | 0.13804 | 0.3268 | 1.6607 | 0.47207 | 2.1328 | 66.6667
200 | 0.069021 | 0.1634 | 0.41518 | 0.11802 | 0.53319 | 33.3333
0 | 0 | 0 | 0 | 0 | 0 | 0
| ACT_System Curve (P_sys) | a | b | c
|  | 0.00047987 | 3.3454e-18 | -1.0658e-14
ACT_FanPerformance
| ACT_Fan Speed (RPM) | 1400
|  | ACT_FanCurve_1400RPM (ΔP) | ACT_FanCurve_1400RPM (Power)
| V (m3/h) | ΔP (Pa) | Power (W)
| 400 | 3.3503 | 14.3006
| 366.6667 | 16.3227 | 16.0946
| 333.3333 | 28.9179 | 17.0715
| 301.9381 | 40.8891 | 17.3148
| 300 | 41.5737 | 17.3115
| 266.6667 | 51.3618 | 16.9969
| 233.3333 | 57.2176 | 16.3501
| 200 | 62.673 | 15.5856
| 166.6667 | 76.0939 | 14.8757
| 133.3333 | 108.4197 | 14.3299
| 100 | 168.407 | 13.9881
| 66.6667 | 255.3768 | 13.8271
| 33.3333 | 349.4648 | 13.7816
| 0 | 399.3752 | 13.778
| ACT_Fan Curve (P_fan) | a | b | c | d | e | f | g
|  | -2.5278e-12 | 3.7437e-09 | -2.1262e-06 | 0.0005605 | -0.061376 | 2.6439e-14 | 399.3752
| ACT_Fan Curve (Power_fan) | a | b | c | d | e | f | g
|  | 1.3884e-14 | -1.3877e-11 | 3.3498e-09 | -8.8676e-20 | 7.4219e-18 | -2.0048e-16 | 13.778
Working Point
| ACT_SystemCurve working pressure (Pa) | ACT_FanCurve working pressure (Pa) | Supplied Air volume flow rate/fan (m3/h) | No of fans | Total Supplied Volume Flow Rate (m3/h)
| 42.4576 | 42.4585 | 297.4503 | 6 | 1784.702
| Difference between curves |  |  |  | Total Inlet Mass Flow Rate (kg/s)
| 7.9323e-07 |  |  |  | 0.61591
Total fan Power Consmption(W)
103.8257
Note on H15: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on DeltaP1/DeltaP2=(V2/V1)^2
Note on D35: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on Catalog data for 1500RPM. The parameters are recalculated using fan laws stated in ASHRAE
Note on D39: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: actual flow rate per fan
Note on E39: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on: Pact=Pstd*(Rho_act/Rho_std)*(Nact/Nstd)^2
Note on F39: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Wact=Wstd*(Rho_act/Rho_std)*(Nact/Nstd)^3
Note on F62: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Iterative variable by SOLVER
Note on D65: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: the objective of SOLVER

## Evap_Num_5x4_ST_3c_V2
Test 24 Air-side Results: Evap_Num_5x4_ST_3c_V2
Vact | 1811.6284 | kg/h
mact | 0.6252 | kg/s
Vstd | 1875.6 | kg/h
∆P_Evap | 27.422 | Pa
k (Evaporator Fan/Pump Duct Pressure Loss Coefficient) | 31.6472 | Pa.S2/kg.m3
∆P_Duct | 9.5967 | Pa
Actual Air Density @ Tair_in for Evap. | 1.2424 | kg/m3
Standard Air Density (Rho_std) | 1.2 | kg/m3
Actual Air Density @ Tair_out for Evap. | 1.289 | kg/m3
Face Area (m2) | 0.34 | m2
ACT_SystemCurve (Evap_Num_5x4_ST_3c_V2 )
Vact (m3/h) | mact (kg/s) | uact (m/s) | ∆P_Evap_Act (pa) | ∆P_Duct_Act (pa) | ∆P_Tot_Act (Pa) | Vact/fan (m3/h)
2400 | 0.82825 | 1.9608 | 48.1264 | 16.8425 | 64.9689 | 400
2200 | 0.75923 | 1.7974 | 40.4395 | 14.1524 | 54.5919 | 366.6667
2000 | 0.69021 | 1.634 | 33.4211 | 11.6962 | 45.1173 | 333.3333
1811.6284 | 0.6252 | 1.4801 | 27.422 | 9.5967 | 37.0187 | 301.9381
1800 | 0.62119 | 1.4706 | 27.0711 | 9.4739 | 36.545 | 300
1600 | 0.55217 | 1.3072 | 21.3895 | 7.4855 | 28.8751 | 266.6667
1400 | 0.48315 | 1.1438 | 16.3763 | 5.7311 | 22.1075 | 233.3333
1200 | 0.41413 | 0.98039 | 12.0316 | 4.2106 | 16.2422 | 200
1000 | 0.3451 | 0.81699 | 8.3553 | 2.924 | 11.2793 | 166.6667
800 | 0.27608 | 0.65359 | 5.3474 | 1.8714 | 7.2188 | 133.3333
600 | 0.20706 | 0.4902 | 3.0079 | 1.0527 | 4.0606 | 100
400 | 0.13804 | 0.3268 | 1.3368 | 0.46785 | 1.8047 | 66.6667
200 | 0.069021 | 0.1634 | 0.33421 | 0.11696 | 0.45117 | 33.3333
0 | 0 | 0 | 0 | 0 | 0 | 0
| ACT_System Curve (P_sys) | a | b | c
|  | 0.00040606 | -4.5625e-17 | 7.1054e-15
ACT_FanPerformance
| ACT_Fan Speed (RPM) | 1400
|  | ACT_FanCurve_1400RPM (ΔP) | ACT_FanCurve_1400RPM (Power)
| V (m3/h) | ΔP (Pa) | Power (W)
| 400 | 3.3805 | 14.4296
| 366.6667 | 16.47 | 16.2398
| 333.3333 | 29.1788 | 17.2255
| 301.9381 | 41.258 | 17.471
| 300 | 41.9488 | 17.4677
| 266.6667 | 51.8253 | 17.1502
| 233.3333 | 57.7338 | 16.4976
| 200 | 63.2385 | 15.7262
| 166.6667 | 76.7805 | 15.0099
| 133.3333 | 109.3979 | 14.4592
| 100 | 169.9265 | 14.1143
| 66.6667 | 257.681 | 13.9519
| 33.3333 | 352.6179 | 13.9059
| 0 | 402.9787 | 13.9023
| ACT_Fan Curve (P_fan) | a | b | c | d | e | f | g
|  | -2.5506e-12 | 3.7775e-09 | -2.1453e-06 | 0.00056555 | -0.06193 | -1.1746e-13 | 402.9787
| ACT_Fan Curve (Power_fan) | a | b | c | d | e | f | g
|  | 1.401e-14 | -1.4002e-11 | 3.38e-09 | 2.4268e-19 | -2.4481e-17 | 9.8789e-16 | 13.9023
Working Point
| ACT_SystemCurve working pressure (Pa) | ACT_FanCurve working pressure (Pa) | Supplied Air volume flow rate/fan (m3/h) | No of fans | Total Supplied Volume Flow Rate (m3/h)
| 38.7273 | 38.7276 | 308.8275 | 6 | 1852.9649
| Difference between curves |  |  |  | Total Inlet Mass Flow Rate (kg/s)
| 8.1369e-08 |  |  |  | 0.63947
Total fan Power Consmption(W)
104.8004
Note on H16: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on DeltaP1/DeltaP2=(V2/V1)^2
Note on D36: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on Catalog data for 1500RPM. The parameters are recalculated using fan laws stated in ASHRAE
Note on D40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: actual flow rate per fan
Note on E40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on: Pact=Pstd*(Rho_act/Rho_std)*(Nact/Nstd)^2
Note on F40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Wact=Wstd*(Rho_act/Rho_std)*(Nact/Nstd)^3
Note on F63: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Iterative variable by SOLVER
Note on D66: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: the objective of SOLVER

## Evap_Num_5x4_ST_9c_V4
Test 24 Air-side Results: Evap_Num_5x4_ST_9c_V4
Vact | 1811.6284 | kg/h
mact | 0.6252 | kg/s
Vstd | 1875.6 | kg/h
∆P_Evap | 16.951 | Pa
k (Evaporator Fan/Pump Duct Pressure Loss Coefficient) | 31.6472 | Pa.S2/kg.m3
∆P_Duct | 9.5596 | Pa
Actual Air Density @ Tair_in for Evap. | 1.2424 | kg/m3
Standard Air Density (Rho_std) | 1.2 | kg/m3
Actual Air Density @ Tair_out for Evap. | 1.294 | kg/m3
Face Area (m2) | 0.34 | m2
ACT_SystemCurve (Evap_Num_5x4_ST_9c_V4)
Vact (m3/h) | mact (kg/s) | uact (m/s) | ∆P_Evap_Act (pa) | ∆P_Duct_Act (pa) | ∆P_Tot_Act (Pa) | Vact/fan (m3/h)
2400 | 0.82825 | 1.9608 | 29.7495 | 16.7774 | 46.5269 | 400
2200 | 0.75923 | 1.7974 | 24.9978 | 14.0977 | 39.0955 | 366.6667
2000 | 0.69021 | 1.634 | 20.6594 | 11.651 | 32.3103 | 333.3333
1811.6284 | 0.6252 | 1.4801 | 16.951 | 9.5596 | 26.5106 | 301.9381
1800 | 0.62119 | 1.4706 | 16.7341 | 9.4373 | 26.1714 | 300
1600 | 0.55217 | 1.3072 | 13.222 | 7.4566 | 20.6786 | 266.6667
1400 | 0.48315 | 1.1438 | 10.1231 | 5.709 | 15.8321 | 233.3333
1200 | 0.41413 | 0.98039 | 7.4374 | 4.1944 | 11.6317 | 200
1000 | 0.3451 | 0.81699 | 5.1648 | 2.9127 | 8.0776 | 166.6667
800 | 0.27608 | 0.65359 | 3.3055 | 1.8642 | 5.1697 | 133.3333
600 | 0.20706 | 0.4902 | 1.8593 | 1.0486 | 2.9079 | 100
400 | 0.13804 | 0.3268 | 0.82637 | 0.46604 | 1.2924 | 66.6667
200 | 0.069021 | 0.1634 | 0.20659 | 0.11651 | 0.3231 | 33.3333
0 | 0 | 0 | 0 | 0 | 0 | 0
| ACT_System Curve (P_sys) | a | b | c
|  | 0.00029079 | -4.3784e-17 | 3.5527e-15
ACT_FanPerformance
| ACT_Fan Speed (RPM) | 1400
|  | ACT_FanCurve_1400RPM (ΔP) | ACT_FanCurve_1400RPM (Power)
| V (m3/h) | ΔP (Pa) | Power (W)
| 400 | 3.3937 | 14.4856
| 366.6667 | 16.5339 | 16.3028
| 333.3333 | 29.292 | 17.2923
| 301.9381 | 41.4181 | 17.5388
| 300 | 42.1115 | 17.5354
| 266.6667 | 52.0263 | 17.2168
| 233.3333 | 57.9578 | 16.5616
| 200 | 63.4838 | 15.7872
| 166.6667 | 77.0784 | 15.0682
| 133.3333 | 109.8223 | 14.5153
| 100 | 170.5856 | 14.1691
| 66.6667 | 258.6805 | 14.006
| 33.3333 | 353.9857 | 13.9599
| 0 | 404.5419 | 13.9563
| ACT_Fan Curve (P_fan) | a | b | c | d | e | f | g
|  | -2.5605e-12 | 3.7922e-09 | -2.1537e-06 | 0.00056775 | -0.06217 | -1.1902e-13 | 404.5419
| ACT_Fan Curve (Power_fan) | a | b | c | d | e | f | g
|  | 1.4064e-14 | -1.4057e-11 | 3.3931e-09 | 2.6823e-19 | -2.6555e-17 | 1.0484e-15 | 13.9563
Working Point
| ACT_SystemCurve working pressure (Pa) | ACT_FanCurve working pressure (Pa) | Supplied Air volume flow rate/fan (m3/h) | No of fans | Total Supplied Volume Flow Rate (m3/h)
| 31.325 | 31.325 | 328.2112 | 6 | 1969.2673
| Difference between curves |  |  |  | Total Inlet Mass Flow Rate (kg/s)
| 1.8363e-10 |  |  |  | 0.6796
Total fan Power Consmption(W)
104.2466
Note on H16: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on DeltaP1/DeltaP2=(V2/V1)^2
Note on D36: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on Catalog data for 1500RPM. The parameters are recalculated using fan laws stated in ASHRAE
Note on D40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: actual flow rate per fan
Note on E40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on: Pact=Pstd*(Rho_act/Rho_std)*(Nact/Nstd)^2
Note on F40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Wact=Wstd*(Rho_act/Rho_std)*(Nact/Nstd)^3
Note on F63: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Iterative variable by SOLVER
Note on D66: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: the objective of SOLVER

## Evap_Num_16x4_ST_3c_V5_1400RPM
Test 24 Air-side Results: Evap_Num_16x4_ST_3c_V5_1400RPM
Vact | 1811.6284 | kg/h
mact | 0.6252 | kg/s
Vstd | 1875.6 | kg/h
∆P_Evap | 47.987 | Pa
k (Evaporator Fan/Pump Duct Pressure Loss Coefficient) | 31.6472 | Pa.S2/kg.m3
∆P_Duct | 9.5967 | Pa
Actual Air Density @ Tair_in for Evap. | 1.2424 | kg/m3
Standard Air Density (Rho_std) | 1.2 | kg/m3
Actual Air Density @ Tair_out for Evap. | 1.289 | kg/m3
Face Area (m2) | 0.34 | m2
ACT_SystemCurve (Evap_Num_16x4_ST_3c_V5_1400RPM)
Vact (m3/h) | mact (kg/s) | uact (m/s) | ∆P_Evap_Act (pa) | ∆P_Duct_Act (pa) | ∆P_Tot_Act (Pa) | Vact/fan (m3/h)
2400 | 0.82825 | 1.9608 | 84.2186 | 16.8425 | 101.061 | 400
2200 | 0.75923 | 1.7974 | 70.767 | 14.1524 | 84.9194 | 366.6667
2000 | 0.69021 | 1.634 | 58.4851 | 11.6962 | 70.1813 | 333.3333
1811.6284 | 0.6252 | 1.4801 | 47.987 | 9.5967 | 57.5837 | 301.9381
1800 | 0.62119 | 1.4706 | 47.3729 | 9.4739 | 56.8468 | 300
1600 | 0.55217 | 1.3072 | 37.4305 | 7.4855 | 44.916 | 266.6667
1400 | 0.48315 | 1.1438 | 28.6577 | 5.7311 | 34.3888 | 233.3333
1200 | 0.41413 | 0.98039 | 21.0546 | 4.2106 | 25.2653 | 200
1000 | 0.3451 | 0.81699 | 14.6213 | 2.924 | 17.5453 | 166.6667
800 | 0.27608 | 0.65359 | 9.3576 | 1.8714 | 11.229 | 133.3333
600 | 0.20706 | 0.4902 | 5.2637 | 1.0527 | 6.3163 | 100
400 | 0.13804 | 0.3268 | 2.3394 | 0.46785 | 2.8073 | 66.6667
200 | 0.069021 | 0.1634 | 0.58485 | 0.11696 | 0.70181 | 33.3333
0 | 0 | 0 | 0 | 0 | 0 | 0
| ACT_System Curve (P_sys) | a | b | c
|  | 0.00063163 | -2.3071e-18 | -7.1054e-15
ACT_FanPerformance
| ACT_Fan Speed (RPM) | 1400
|  | ACT_FanCurve_1400RPM (ΔP) | ACT_FanCurve_1400RPM (Power)
| V (m3/h) | ΔP (Pa) | Power (W)
| 400 | 3.3805 | 14.4296
| 366.6667 | 16.47 | 16.2398
| 333.3333 | 29.1788 | 17.2255
| 301.9381 | 41.258 | 17.471
| 300 | 41.9488 | 17.4677
| 266.6667 | 51.8253 | 17.1502
| 233.3333 | 57.7338 | 16.4976
| 200 | 63.2385 | 15.7262
| 166.6667 | 76.7805 | 15.0099
| 133.3333 | 109.3979 | 14.4592
| 100 | 169.9265 | 14.1143
| 66.6667 | 257.681 | 13.9519
| 33.3333 | 352.6179 | 13.9059
| 0 | 402.9787 | 13.9023
| ACT_Fan Curve (P_fan) | a | b | c | d | e | f | g
|  | -2.5506e-12 | 3.7775e-09 | -2.1453e-06 | 0.00056555 | -0.06193 | -1.1746e-13 | 402.9787
| ACT_Fan Curve (Power_fan) | a | b | c | d | e | f | g
|  | 1.401e-14 | -1.4002e-11 | 3.38e-09 | 2.4268e-19 | -2.4481e-17 | 9.8789e-16 | 13.9023
Working Point
| ACT_SystemCurve working pressure (Pa) | ACT_FanCurve working pressure (Pa) | Supplied Air volume flow rate/fan (m3/h) | No of fans | Total Supplied Volume Flow Rate (m3/h)
| 48.8843 | 48.8843 | 278.1973 | 6 | 1669.1839
| Difference between curves |  |  |  | Total Inlet Mass Flow Rate (kg/s)
| 1.0128e-13 |  |  |  | 0.57604
Total fan Power Consmption(W)
103.8576
Note on H16: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on DeltaP1/DeltaP2=(V2/V1)^2
Note on D36: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on Catalog data for 1500RPM. The parameters are recalculated using fan laws stated in ASHRAE
Note on D40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: actual flow rate per fan
Note on E40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on: Pact=Pstd*(Rho_act/Rho_std)*(Nact/Nstd)^2
Note on F40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Wact=Wstd*(Rho_act/Rho_std)*(Nact/Nstd)^3
Note on F63: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Iterative variable by SOLVER
Note on D66: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: the objective of SOLVER

## Evap_Num_16x4_ST_3c_V5_1600RPM
Test 24 Air-side Results: Evap_Num_16x4_ST_3c_V5_1600RPM
Vact | 1811.6284 | kg/h
mact | 0.6252 | kg/s
Vstd | 1875.6 | kg/h
∆P_Evap | 47.987 | Pa
k (Evaporator Fan/Pump Duct Pressure Loss Coefficient) | 31.6472 | Pa.S2/kg.m3
∆P_Duct | 9.5967 | Pa
Actual Air Density @ Tair_in for Evap. | 1.2424 | kg/m3
Standard Air Density (Rho_std) | 1.2 | kg/m3
Actual Air Density @ Tair_out for Evap. | 1.289 | kg/m3
Face Area (m2) | 0.34 | m2
ACT_SystemCurve (Evap_Num_16x4_ST_3c_V5_1600RPM)
Vact (m3/h) | mact (kg/s) | uact (m/s) | ∆P_Evap_Act (pa) | ∆P_Duct_Act (pa) | ∆P_Tot_Act (Pa) | Vact/fan (m3/h)
2400 | 0.82825 | 1.9608 | 84.2186 | 16.8425 | 101.061 | 400
2200 | 0.75923 | 1.7974 | 70.767 | 14.1524 | 84.9194 | 366.6667
2000 | 0.69021 | 1.634 | 58.4851 | 11.6962 | 70.1813 | 333.3333
1811.6284 | 0.6252 | 1.4801 | 47.987 | 9.5967 | 57.5837 | 301.9381
1800 | 0.62119 | 1.4706 | 47.3729 | 9.4739 | 56.8468 | 300
1600 | 0.55217 | 1.3072 | 37.4305 | 7.4855 | 44.916 | 266.6667
1400 | 0.48315 | 1.1438 | 28.6577 | 5.7311 | 34.3888 | 233.3333
1200 | 0.41413 | 0.98039 | 21.0546 | 4.2106 | 25.2653 | 200
1000 | 0.3451 | 0.81699 | 14.6213 | 2.924 | 17.5453 | 166.6667
800 | 0.27608 | 0.65359 | 9.3576 | 1.8714 | 11.229 | 133.3333
600 | 0.20706 | 0.4902 | 5.2637 | 1.0527 | 6.3163 | 100
400 | 0.13804 | 0.3268 | 2.3394 | 0.46785 | 2.8073 | 66.6667
200 | 0.069021 | 0.1634 | 0.58485 | 0.11696 | 0.70181 | 33.3333
0 | 0 | 0 | 0 | 0 | 0 | 0
| ACT_System Curve (P_sys) | a | b | c
|  | 0.00063163 | -2.3071e-18 | -7.1054e-15
ACT_FanPerformance
| ACT_Fan Speed (RPM) | 1600
|  | ACT_FanCurve_1600RPM (ΔP) | ACT_FanCurve_1600RPM (Power)
| V (m3/h) | ΔP (Pa) | Power (W)
| 400 | 4.4154 | 21.5392
| 366.6667 | 21.5118 | 24.2414
| 333.3333 | 38.1111 | 25.7127
| 301.9381 | 53.8881 | 26.0791
| 300 | 54.7903 | 26.0742
| 266.6667 | 67.6901 | 25.6004
| 233.3333 | 75.4075 | 24.6262
| 200 | 82.5973 | 23.4747
| 166.6667 | 100.2848 | 22.4055
| 133.3333 | 142.8871 | 21.5835
| 100 | 221.9448 | 21.0686
| 66.6667 | 336.5629 | 20.8261
| 33.3333 | 460.5622 | 20.7576
| 0 | 526.3395 | 20.7522
| ACT_Fan Curve (P_fan) | a | b | c | d | e | f | g
|  | -3.3314e-12 | 4.9339e-09 | -2.8021e-06 | 0.00073868 | -0.080888 | -1.5712e-13 | 526.3395
| ACT_Fan Curve (Power_fan) | a | b | c | d | e | f | g
|  | 2.0912e-14 | -2.0902e-11 | 5.0454e-09 | 3.8787e-19 | -3.9203e-17 | 1.6068e-15 | 20.7522
Working Point
| ACT_SystemCurve working pressure (Pa) | ACT_FanCurve working pressure (Pa) | Supplied Air volume flow rate/fan (m3/h) | No of fans | Total Supplied Volume Flow Rate (m3/h)
| 55.917 | 55.9174 | 297.5364 | 6 | 1785.2184
| Difference between curves |  |  |  | Total Inlet Mass Flow Rate (kg/s)
| 1.7991e-07 |  |  |  | 0.61609
Total fan Power Consmption(W)
156.3828
Note on H16: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on DeltaP1/DeltaP2=(V2/V1)^2
Note on D36: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on Catalog data for 1500RPM. The parameters are recalculated using fan laws stated in ASHRAE
Note on D40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: actual flow rate per fan
Note on E40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Based on: Pact=Pstd*(Rho_act/Rho_std)*(Nact/Nstd)^2
Note on F40: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Wact=Wstd*(Rho_act/Rho_std)*(Nact/Nstd)^3
Note on F63: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: Iterative variable by SOLVER
Note on D66: ABDELRAHMAN HUSSEIN ABDELHALIM HASSAN: the objective of SOLVER

## STD_Fan_Performance_1500RPM
STD_Fan curve at 1500 rpm
| N | 1500 | RPM
| Q | ΔP | Q | Power
| m3/h | Pa | m3/h | W
| 200 | 71.7 | 214 | 18
| 250 | 61.7 | 321 | 20
| 300 | 51.7 | 383 | 19
| 350 | 34 | 435.71 | 16
| 400 | 15
| 435.71 | 0
Pstd | a | b | c | d | e | f | g
| -1.8018e-12 | 2.8592e-09 | -1.7398e-06 | 0.0004914 | -0.057654 | 0 | 430.6623
Power_std | a | b | c | d | e | f | g
| 1.0604e-14 | -1.1355e-11 | 2.9369e-09 | 0 | 0 | 0 | 15.9186
STD_FanCurve_1500RPM (Based on Functions)
| Vact | Vstd | Pstd | Power_std
| 400 | 428.5714 | 3.6128 | 16.5224
| 366.6667 | 392.8571 | 17.6014 | 18.5951
| 333.3333 | 357.1429 | 31.1833 | 19.7238
| 301.9381 | 323.5051 | 44.0924 | 20.0049
| 300 | 321.4286 | 44.8306 | 20.0011
| 266.6667 | 285.7143 | 55.3855 | 19.6376
| 233.3333 | 250 | 61.7 | 18.8903
| 200 | 214.2857 | 67.5828 | 18.007
| 166.6667 | 178.5714 | 82.0552 | 17.1869
| 133.3333 | 142.8571 | 116.9133 | 16.5563
| 100 | 107.1429 | 181.6 | 16.1614
| 66.6667 | 71.4286 | 275.383 | 15.9754
| 33.3333 | 35.7143 | 376.8418 | 15.9228
| 0 | 0 | 430.6623 | 15.9186