## old
[5 empty] | 1 complete running cycle | [12 empty] | C1 | C2 | C3 | [5 empty] | 24h |  |  |  |  | C1 | C2 | C3 | C1 | C2 | C3 | C1 | C2 | C3
Test # | Spec | Condensing Temp | Gen | Ceiling | Product Temp [°C] |  |  |  | Temp class | COP compr | Qevap Qcond hevap in + Select massflow | Qevap,balance | DQevap % | Pcp,meas | Qevap,select0K | Pcp,sel | Qcond | xcd,out (mselect) | xcd,out (mselect) | xcd,out (mselect) | DPower % | DQevap % | Fans speed | Fans power | Aux power | TEC | EEI | Energy Label | Tair,in | Tair,out | C1: T disch; C1: T evap [°C]; C1: SH evap [K] | Tw,in [°C] | Tw,out [°C] | Tcond1 [°C] | Tcond2 [°C] | Tcond3 [°C] |  |  | Dhevap | Massflow select | Massflow select corrected | Massflow KlasBerglof
- |  | °C | - |  | AVG | MAX | MIN | MEDIAN |  | - | kW | [33 empty] | hsuc | hdis | kJ/kg
5 |  | 35 | 1 | no | 6.3615 | 10.2279 | 2.6823 | 5.8256 | 3H2 | 2.1485 | 5.7484 | 6.2924 | 8.646% | 2.6752 | 7.4884 | 2.366 | 8.8339 | 15.06% | 6.936% | 18.14% | 13.07% | -23.24% | 1400 | 64.6927 | 83.9392 | 63.3463 | 49.77% | B | 10.4999 | 1.635 | 72.0413 | 72.3941 | 69.6783 | -8.9549 | -7.161 | -8.1797 | 15.337 | 11.8726 | 13.7877 | 30 | 35 | 33.6327 | 34.8602 | 33.9985 | 589139.9303 | 689222.9554 | 226.3757 | 26.5031 |  | 25.3932
4 |  | 55 |  | no | 6.135 | 9.6358 | 2.7047 | 5.9205 | 3H2 | 1.2557 | 4.7521 | 4.1808 | -13.66% | 3.7851 | 7.002 | 3.5179 | 7.7766 | 34.8% | 19.21% | 28.32% | 7.595% | -32.13% | 1400 | 69.2289 | 77.7429 | 82.6858 | 65% | C | 10.8275 | 4.3593 | 88.9258 | 91.0364 | 86.2026 | -3.6601 | -2.6571 | -2.9118 | 11.489 | 7.5386 | 9.211 | 50 | 55 | 52.7913 | 54.5724 | 53.3853 | 588778.3686 | 709311.8748 | 159.2928 | 30.2294 |  | 29.8324
18 | 1400rpm | 35 | 2 | no | 5.2357 | 10.673 | 0.44621 | 4.6862 | 3H2 | 2.257 | 6.0656 | 5.9796 | -1.439% | 2.6874 | 6.8147 | 2.3913 | 8.5326 | 8.36% | 7.011% | 14.43% | 12.38% | -10.99% | 1400 | 74.2767 |  |  |  |  | 8.6029 | -0.66092 | 68.0373 | 74.2648 | 67.7715 | -9.8579 | -10.2931 | -10.1764 | 8.5153 | 9.5411 | 8.8983 | 30.0439 | 34.8956 | 34.8781 | 35.2853 | 34.2067 | 576137.0498 | 679655.4897 | 245.9458 | 24.4702 |  | 24.6624
19 | 1600rpm | 35 |  | no | 5.6329 | 10.4853 | 1.7782 | 5.0485 | 3H2 | 2.3766 | 6.4161 | 6.381 | -0.551% | 2.6997 | 7.4904 | 2.3876 | 8.9457 | 10.41% | 8.125% | 19.7% | 13.07% | -14.34% | 1400 | 108.0987 |  |  |  |  | 8.6497 | 1.3751 | 66.1737 | 71.7174 | 66.4297 | -7.8065 | -8.2374 | -7.8248 | 8.309 | 9.4106 | 8.508 | 30.0439 | 34.9136 | 34.6318 | 35.3505 | 33.8695 | 578204.0493 | 675871.7019 | 244.336 | 26.6106 |  | 26.2595
19 | 1200rpm | 35 |  | no | 5.6486 | 11.1977 | 0.014087 | 5.0331 | 3H2 | 2.2072 | 5.9173 | 5.8348 | -1.414% | 2.6808 | 6.6338 | 2.3941 | 8.3815 | 6.881% | 6.991% | 15.53% | 11.97% | -10.8% | 1400 | 50.3461 |  |  |  |  | 8.8083 | -1.5664 | 68.5011 | 74.7776 | 69.1454 | -10.5664 | -10.8067 | -10.7119 | 8.4458 | 9.5499 | 8.781 | 30.0337 | 34.9462 | 35.0164 | 35.3726 | 34.2752 | 575175.7905 | 680533.2934 | 244.7958 | 23.9029 |  | 24.1723
19 | 1800rpm | 35 |  | no | 6.1545 | 10.5836 | 2.8812 | 5.6409 | 3H2 | 2.4515 | 6.656 | 6.6072 | -0.7392% | 2.7151 | 7.7611 | 2.3899 | 9.1866 | 10.43% | 6.701% | 20.3% | 13.61% | -14.24% | 1400 | 155.7204 |  |  |  |  | 8.0676 | 1.8843 | 65.1599 | 69.3839 | 65.2164 | -6.9254 | -7.4145 | -6.9657 | 7.9862 | 8.5324 | 8.2377 | 30.0548 | 34.9907 | 34.72 | 35.4187 | 33.8019 | 578674.507 | 673623.8047 | 245.0151 | 27.484 |  | 27.1658
24 |  | 35 |  | no | 5.7463 | 10.3017 | 1.5572 | 4.8645 | 3H2 | 2.4604 | 6.588 | 6.5225 | -1.004% | 2.6769 | 7.1648 | 2.387 | 9.0656 | 4.701% | 2.252% | 15.46% | 12.15% | -8.05% | 1400 | 75.0057 | ? | 61.3801 | 48.23% | B | 8.9661 | 0.26767 | 66.2171 | 71.6853 | 66.8655 | -8.8207 | -9.281 | -8.8811 | 8.0415 | 9.1146 | 8.7035 | 30 | 35 | 34.6618 | 35.3414 | 33.9182 | 576538.7246 | 675939.0658 | 257.505 | 25.569 |  | 25.5841
26 |  | 55 |  | no | 6.7074 | 10.852 | 3.0401 | 6.0908 | 3H2 | 1.5092 | 5.3976 | 5.2708 | -2.405% | 3.6785 | 5.9949 | 3.5642 | 8.7654 | 5.152% | 5.241% | 16.19% | 3.207% | -9.963% | 1400 | 74.3579 | ? | 89.0405 | 69.96% | C | 9.2824 | 1.9259 | 89.2405 | 96.6022 | 91.3335 | -6.1536 | -6.591 | -6.1409 | 8.0356 | 9.0786 | 8.327 | 50 | 55 | 54.6326 | 55.2273 | 53.9764 | 579668.8882 | 708056.8473 | 198.3018 | 26.6632 |  | 27.219
27 |  | 35 | 3 | no | 6.558 | 10.8892 | 2.9691 | 6.2818 | 3H2 | 2.4031 | 5.9858 | 5.9356 | -0.8453% | 2.4463 | 8.3308 | 2.2597 | 8.2596 | 25.72% | 26.72% | 19.88% | 8.258% | -28.15% | 1400 | 75.341 | ? | 58.3901 | 45.88% | B | 8.9833 | 2.1215 | 62.0416 | 61.6007 | 60.9358 | -6.0308 | -6.0656 | -6.4788 | 8.9223 | 8.7556 | 8.3801 | 30 | 35 | 31.1353 | 31.7034 | 32.8211 | 581382.6765 | 670014.7578 | 228.2879 | 28.6194 |  | 26.2204
28 |  | 55 |  | no | 8.2837 | 11.9833 | 5.3233 | 8.1676 | 3H2 | 1.2308 | 4.4625 | 4.3241 | -3.2% | 3.6257 | 7.1484 | 3.4973 | 7.7685 | 32.67% | 40.05% | 21.4% | 3.67% | -37.57% | 1400 | 74.2241 | ? | 81.2271 | 63.82% | C | 9.8189 | 4.2071 | 86.093 | 85.4823 | 85.3854 | -2.5885 | -2.5392 | -3.0034 | 7.5441 | 7.6982 | 7.9963 | 50 | 55 | 52.8957 | 52.9327 | 53.9602 | 582959.3933 | 702612.466 | 155.0196 | 30.6712 |  | 28.7864
34 |  | 40 |  | yes | 5.9412 | 10.7066 | 2.0722 | 5.8471 | 3H2 | 2.0434 | 5.5082 | 5.3878 | -2.234% | 2.6954 | 7.3833 | 2.5499 | 7.9484 | 27.32% | 18.1% | 19.34% | 5.706% | -25.4% | 1400 | 75.2697 | ? | 63.7256 | 50.07% | C | 8.4213 | 1.1862 | 68.0209 | 69.2337 | 68.1101 | -6.8011 | -7.5342 | -7.5961 | 8.221 | 8.3756 | 8.5301 | 35 | 40 | 36.758 | 38.7316 | 38.1766 | 579234.6575 | 677996.671 | 212.4509 | 27.0396 |  | 25.9268
35 |  | 35 |  | yes | 5.3626 | 10.5443 | 0.9843 | 5.3635 | 3H2 | 2.3495 | 5.7362 | 5.6373 | -1.753% | 2.4412 | 7.35 | 2.2972 | 7.9565 | 24.68% | 13.87% | 17.31% | 6.271% | -21.96% | 1400 | [5 empty] | 7.7588 | -0.049279 | 62.5888 | 63.9618 | 63.1567 | -8.4323 | -9.2062 | -9.2546 | 8.207 | 8.1914 | 8.5815 | 30 | 35 | 31.3904 | 33.6283 | 33.0746 | 577286.5119 | 670960.7737 | 231.6941 | 25.728 |  | 24.7575
Test # | LMTD C1 [K] | LMTD C2 [K] | LMTD C3 [K] | cpw | Temperatures - C1 Evap in (deg C) | Temperatures - C1 Evap out (deg C) | Temperatures - C1 discharge (deg C) | Temperatures - C1 liquid / cond out (deg C) | Temperatures - C1 condensor in (deg C) | Pressures - C1 discharge pressure (bar) | Pressures - C1 liquid line pressure (bar) | Pressures - C1 evap in pressure (bar) | Pressures - C1 evap out pressure (bar) | h cond in C1 [kJ/kg] | TVAP,SAT HP C1 [°C] | hVAP,SAT HP C1 [kJ/kg] | hVAP,SAT LP C1 [kJ/kg] | hLIQ,SAT LP C1 [kJ/kg] | hDISCHARGE C1 [kJ/kg] | Q_DESH C1 [kW] | % DESH C1 | xEVAP,IN C1 | massflow R290 C1 (coeffs) [g/s] | v_MAP/v_REAL | TW,PINCH C1 [°C] | DTPINCH C1 [°C] | Q_cond_water C1 [kW] | h_cond_out C1 [kJ/kg] | h_LIQ,SAT HP C1 [kJ/kg] | xCOND,OUT C1 | Qevap C1 [kW] | h_evap,out C1 [kJ/kg] | DTSH C1 | DTSC C1 | Tsat C1 discharge [°C] | Tsat C1 liquid line Tcond [°C] | Tsat C1 evap in [°C] | Tsat C1 evap out (dew) Tevap [°C] | DT = TCOND - Tw,out C1 | DT = TAIR,IN - TEVAP(dew) C1 | DTGLIDE = TREF,IN - TEVAP(dew) C1 | Temperatures - C2 Evap in (deg C) | Temperatures - C2 Evap out (deg C) | Temperatures - C2 discharge (deg C) | Temperatures - C2 liquid (deg C) | Temperatures - C2 condensor in (deg C) | Pressures - C2 discharge pressure (bar) | Pressures - C2 liquid line pressure (bar) | Pressures - C2 evap in pressure (bar) | Pressures - C2 evap out pressure (bar) | h cond in C2 [kJ/kg] | TVAP,SAT HP C2 [°C] | hVAP,SAT HP C2 [kJ/kg] | hVAP,SAT LP C2 [kJ/kg] | hLIQ,SAT LP C2 [kJ/kg] | hDISCHARGE C2 [kJ/kg] | Q_DESH C2 [kW] | % DESH C2 | xEVAP,IN C2 | massflow R290 C2 (coeffs) [g/s] | v_MAP/v_REAL | TW,PINCH C2 [°C] | DTPINCH C2 [°C] | Q_cond_water C2 [kW] | h_cond_out C2 [kJ/kg] | h_LIQ,SAT HP C2 [kJ/kg] | xCOND,OUT C2 | Qevap C2 [kW] | h_evap,out C2 [kJ/kg] | DTSH C2 | DTSC C2 | Tsat C2 discharge [°C] | Tsat C2 liquid line [°C] | Tsat C2 evap in [°C] | Tsat C2 evap out (dew) [°C] | DT = TCOND - Tw,out C2 | DT = TAIR,IN - TEVAP(dew) C2 | DTGLIDE = TREF,IN - TEVAP(dew) C2 | Temperatures - C3 Evap in (deg C) | Temperatures - C3 Evap out (deg C) | Temperatures - C3 discharge (deg C) | Temperatures - C3 liquid (deg C) | Temperatures - C3 condensor in (deg C) | Pressures - C3 discharge pressure (bar) | Pressures - C3 liquid line pressure (bar) | Pressures - C3 evap in pressure (bar) | Pressures - C3 evap out pressure (bar) | h cond in C3 [kJ/kg] | TVAP,SAT C3 [°C] | hVAP,SAT HP C3 [kJ/kg] | hVAP,SAT LP C3 [kJ/kg] | hLIQ,SAT LP C3 [kJ/kg] | hDISCHARGE C3 [kJ/kg] | Q_DESH C3 [kW] | % DESH C3 | xEVAP,IN C3 | massflow R290 C3 (coeffs) [g/s] | v_MAP/v_REAL | TW,PINCH C3 [°C] | DTPINCH C3 [°C] | Qcond,water C3 [kW] | hcond,out C3 [kJ/kg] | h_LIQ,SAT HP C3 [kJ/kg] | xCOND,OUT C3 | Qevap C3 [kW] | h_evap,out C3 [kJ/kg] | DTSH C3 | DTSC C3 | Tsat C3 discharge [°C] | Tsat C3 liquid line [°C] | Tsat C3 evap in [°C] | Tsat C3 evap out (dew) [°C] | DT = TCOND - Tw,out C3 | DT = TAIR,IN - TEVAP(dew) C3 | DTGLIDE = TREF,IN - TEVAP(dew) C3 | Temperatures - water in (deg C) | Temperatures - C1 water out (deg C) | Temperatures - C2 water out (deg C) | Temperatures - C3 water out (deg C) | Water mass flow (g/s) | Temperatures - air out left (deg C) | Temperatures - air out mid (deg C) | Temperatures - air out right (deg C) | Temperatures - air in left (deg C) | Temperatures - air in mid (deg C) | Temperatures - air in right (deg C) | Temperatures - ambient temp (deg C) | Relative Humidity | Absolute Pressure (Pa) | Temperatures - BL 1.1 (deg C) | Temperatures - BL 1.2 (deg C) | Temperatures - BL 1.3 (deg C) | Temperatures - BL 1.4 (deg C) | Temperatures - BL 1.5 (deg C) | Temperatures - BL 1.6 (deg C) | Temperatures - BL 2.1 (deg C) | Temperatures - BL 2.2 (deg C) | Temperatures - BL 2.3 (deg C) | Temperatures - BL 2.4 (deg C) | Temperatures - BL 2.5 (deg C) | Temperatures - BL 2.6 (deg C) | Temperatures - BL 3.1 (deg C) | Temperatures - BL 3.2 (deg C) | Temperatures - BL 3.3 (deg C) | Temperatures - BL 3.4 (deg C) | Temperatures - BL 3.5 (deg C) | Temperatures - BL 3.6 (deg C) | Temperatures - BL 4.1 (deg C) | Temperatures - BL 4.2 (deg C) | Temperatures - BL 4.3 (deg C) | Temperatures - BL 4.4 (deg C) | Temperatures - BL 4.5 (deg C) | Temperatures - BL 4.6 (deg C) | T_BL avg | T_BL_median | T_BL min | T_BL max | DT air in/out LEFT | DT air in/out MID | DT air in/out RIGHT | Temperatures - air out AVG (deg C) | Temperatures - air in AVG (deg C) | DTAIR IN - OUT | Qevap,TOT | P-E1[W] | P-E2[W] | P-E3[W] | P-E4[W] | P-E5[W] | P-E6[W] | P-SigA[W] | Total P from Chamber [W] | Wh | P1+PsigA | Meas. Difference | T_SAT_ev_in AVG | T_SAT_ev_out AVG | T_su AVG | COP compr | Temperatures - C1 Evap in (deg C) | Temperatures - C1 Evap 1. pass (deg C) | Temperatures - C1 Evap 2. pass (deg C) | Temperatures - C1 Evap 3. pass (deg C) | Temperatures - C1 Evap 4. pass (deg C) | Temperatures - C1 Evap 5. pass (deg C) | Temperatures - C1 Evap out (deg C) | Temperatures - C2 Evap in (deg C) | Temperatures - C2 Evap 1. pass (deg C) | Temperatures - C2 Evap 2. pass (deg C) | Temperatures - C2 Evap 3. pass (deg C) | Temperatures - C2 Evap 4. pass (deg C) | Temperatures - C2 Evap 5. pass (deg C) | Temperatures - C2 Evap out (deg C) | Temperatures - C3 Evap in (deg C) | Temperatures - C3 Evap 1. pass (deg C) | Temperatures - C3 Evap 2. pass (deg C) | Temperatures - C3 Evap 3. pass (deg C) | Temperatures - C3 Evap 4. pass (deg C) | Temperatures - C3 Evap 5. pass (deg C) | Temperatures - C3 Evap out (deg C)
5 | 16.1825 | 17.3286 | 16.4772 | 3.4 | -4.9773 | 6.08 | 72.1586 | 34.7922 | 69.402 | 11.2106 | 10.7939 | 3.1293 | 2.5693 | 682.4246 | 35.0637 | 607.5125 | 606.1981 | 188.6872 | 688.3367 | 0.65828 | 0.23624 | 0.36313 | 8.148 | 0.95086 | 32.9703 | 2.0934 | 2.7875 | 340.3036 | 292.029 | 0.15301 | 2.0242 | 588.6995 | 15.21 | -1.182 | 35.0637 | 33.6102 | -4.5931 | -9.13 | -0.42875 | 19.5837 | 4.1527 | -3.4159 | 4.1459 | 72.4441 | 35.7307 | 70.8625 | 11.6058 | 11.1436 | 3.3121 | 2.773 | 684.4359 | 36.4089 | 608.7125 | 564.0681 | 192.0684 | 687.8479 | 0.69615 | 0.21695 | 0.34293 | 8.7978 | 0.96748 | 33.6108 | 2.7981 | 3.2095 | 319.6465 | 295.8001 | 0.076202 | 2.3301 | 584.3998 | 11.5699 | -0.89866 | 36.4089 | 34.832 | -3.2144 | -7.4241 | 0.05448 | 17.8777 | 4.0082 | 564.0681 | 5.1594 | 69.7467 | 34.564 | 71.2947 | 11.2582 | 10.8974 | 3.1884 | 2.6586 | 686.3505 | 35.2276 | 607.6595 | 563.0192 | 0.63571 | 683.0279 | 0.63571 | 0.22478 | 0.43204 | 8.4371 | 0.95841 | 32.949 | 2.2786 | 2.829 | 351.0462 | 292.4872 | 0.1858 | 1.9886 | 586.6907 | 13.5311 | -0.58956 | 35.2276 | 33.9744 | -4.1428 | -8.3717 | -0.13705 | 18.8254 | 3.9773 | 29.1568 | 34.0389 | 34.7775 | 34.1115 | 504.0316 | 2.0152 | 1.2652 | 1.0838 | 8.9238 | 10.8425 | 11.5947 | 25.4836 | 0.57934 | 990.9201 | 3.4961 | 5.474 | 3.0583 | 2.6833 | 5.5865 | 5.2531 | 4.1214 | 7.3754 | 4.099 | 4.78 | 7.2697 | 7.8689 | 4.744 | 9.1183 | 4.8504 | 5.023 | 8.9728 | 9.551 | 6.6041 | 10.0434 | 6.0647 | 6.8242 | 9.5943 | 10.2283 | 6.3618 | 5.8256 | 2.6833 | 10.2283 | 6.9086 | 9.5773 | 10.511 | 1.4547 | 10.4537 | 8.999 | 5.7422 | 147.6308 | 69.9419 | 64.6957 | 868.0502 | 868.1035 | 937.5509 | 2673.7077 | 2841.479 |  | 2821.3385 | -0.0070863 | -3.9834 | -8.3033 | 5.1284 | 2.1473 | -4.9773 | -12927.0378 | -5.8451 | -6.2632 | -7.3248 | -0.89133 | 6.08 | -3.4159 | -3.5978 | -4.0382 | -4.7596 | -5.4755 | -5.4138 | 4.1459 | -4.3944 | -3.9774 | -5.1822 | -5.8073 | -5.8846 | -4.5441 | 5.1594
4 | 14.341 | 16.6122 | 14.2073 | 3.3561 | 0.82293 | 7.7446 | 88.8698 | 53.5204 | 85.4 | 17.8478 | 17.206 | 3.8856 | 3.2435 | 699.2792 | 54.416 | 622.8168 | 621.7291 | 202.1293 | 707.427 | 0.8116 | 0.33623 | 0.58508 | 9.5922 | 0.96758 | 51.94 | 2.4761 | 2.4139 | 447.629 | 348.7135 | 0.36087 | 1.3528 | 588.6623 | 11.4638 | -0.73156 | 54.416 | 52.7888 | 0.85799 | -3.7192 | -0.5505 | 14.4264 | 4.5421 | 1.7814 | 4.9244 | 91.0022 | 55.0357 | 89.0246 | 18.438 | 17.9097 | 4.0628 | 3.3773 | 706.1479 | 55.8766 | 623.7526 | 569.2359 | 205.0754 | 710.817 | 0.8755 | 0.29278 | 0.55936 | 10.0559 | 0.9863 | 52.8581 | 3.0184 | 2.9903 | 408.7723 | 353.2449 | 0.20527 | 1.7519 | 582.9903 | 7.6495 | -0.46494 | 55.8766 | 54.5707 | 2.0412 | -2.7251 | 0.13179 | 13.4323 | 4.5065 | 569.2359 | 6.1886 | 86.1075 | 52.7792 | 88.4649 | 17.9376 | 17.4384 | 4.0281 | 3.3435 | 706.2283 | 54.6404 | 622.9631 | 568.964 | 0.7724 | 700.6861 | 0.7724 | 0.28149 | 0.61903 | 9.9379 | 0.97873 | 52.3902 | 2.2501 | 2.744 | 430.1161 | 349.4067 | 0.29504 | 1.5434 | 585.4187 | 9.1624 | 0.60373 | 54.6404 | 53.3829 | 1.812 | -2.9738 | -0.58616 | 13.681 | 4.5398 | 48.7337 | 53.3393 | 54.4389 | 53.969 | 468.5502 | 4.2998 | 4.2636 | 4.2387 | 9.3743 | 11.1327 | 11.6146 | 23.9108 | 0.60306 | 985.2164 | 3.6431 | 5.9402 | 2.7741 | 3.0827 | 5.9538 | 6.0047 | 4.5773 | 7.4755 | 3.9234 | 4.448 | 7.3623 | 7.9665 | 4.6115 | 8.7561 | 4.2311 | 4.1609 | 8.697 | 9.0338 | 5.982 | 9.6647 | 5.1071 | 6.0505 | 9.4512 | 9.5022 | 6.1833 | 5.9679 | 2.7741 | 9.6647 | 5.0746 | 6.8691 | 7.376 | 4.2673 | 10.7072 | 6.4399 | 4.6481 | 147.0164 | 69.3007 | 64.6899 | 1246.0612 | 1204.0669 | 1334.6496 | 3784.7826 | 3959.0541 |  | 3931.7991 | -0.0068841 | 1.5704 | -4.943 | 6.2859 | 1.2281
18 | 13.2635 | 12.4893 | 14.5119 | 3.4 | -5.9735 | -1.8313 | 68.0399 | 34.8894 | 63.3606 | 11.3157 | 11.1903 | 2.9826 | 2.4865 | 669.1279 | 35.4224 | 607.8331 | 607.4484 | 185.7866 | 679.1892 | 0.57779 | 0.20474 | 0.32022 | 8.131 | 0.98464 | 34.1927 | 1.2298 | 2.8282 | 320.8157 | 293.0339 | 0.088281 | 2.0683 | 575.2981 | 8.0539 | 0.10354 | 35.4224 | 34.9929 | -5.7861 | -9.8852 | -0.083318 | 18.3984 | 3.9117 | -6.2694 | -0.91827 | 74.1792 | 32.8761 | 71.8216 | 11.5702 | 11.3424 | 3.0091 | 2.4419 | 686.5988 | 36.2879 | 608.6047 | 560.8945 | 186.3021 | 691.6826 | 0.6572 | 0.22446 | 0.34849 | 7.9523 | 0.97828 | 34.1608 | 2.1271 | 2.9313 | 316.7972 | 295.4608 | 0.069087 | 2.0647 | 577.0955 | 9.3624 | 2.6393 | 36.2879 | 35.5153 | -5.5745 | -10.2807 | 0.2566 | 18.794 | 4.0113 | 560.8945 | -1.6297 | 68.0242 | 34.4176 | 69.2098 | 11.2707 | 11.0029 | 3.0025 | 2.4494 | 681.8361 | 35.2692 | 607.6962 | 560.9732 | 0.57247 | 679.2902 | 0.57247 | 0.20876 | 0.40788 | 8.0233 | 0.98205 | 33.8714 | 1.3977 | 2.7452 | 339.0316 | 292.6044 | 0.14739 | 1.8981 | 575.8345 | 8.5806 | -0.074455 | 35.2692 | 34.3431 | -5.6251 | -10.2103 | -0.58478 | 18.7236 | 3.8898 | 30.0378 | 35.0762 | 35.2587 | 34.9279 | 497.6219 | -1.0207 | -1.1343 | 0.33825 | 7.5111 | 8.3974 | 9.6313 | 25.5895 | 0.56294 | 976.9779 | 0.47356 | 3.8031 | 0.40121 | 2.1348 | 3.6687 | 4.6986 | 2.0457 | 6.9203 | 2.4122 | 3.9674 | 5.6719 | 8.8986 | 2.4287 | 8.7661 | 3.062 | 4.6555 | 7.4454 | 10.3627 | 3.9964 | 9.1191 | 4.9975 | 6.5761 | 8.611 | 10.7077 | 5.2427 | 4.6771 | 0.40121 | 10.7077 | 8.5317 | 9.5317 | 9.293 | -0.60557 | 8.5133 | 9.1188 | 6.031 | 77.1202 | 73.0477 | 64.7503 | 880.1875 | 868.4488 | 944.8696 | 2693.5058 | 2874.748 |  | 2770.8779 | -0.036122 | -5.6619 | -10.1058 | -1.4597 | 2.2376 | -5.9735 | -6.1848 | -6.7305 | -7.3573 | -8.1206 | -9.2381 | -1.8313 | -6.2694 | -6.6217 | -7.0299 | -7.7635 | -8.751 | -9.6175 | -0.91827 | -6.3205 | -6.649 | -7.3125 | -7.7362 | -8.5867 | -9.481 | -1.6297
19 / 1600 | 12.926 | 14.3761 | 14.1091 | 3.4 | -3.2513 | 0.665 | 65.9647 | 35.0537 | 61.6928 | 11.3635 | 11.1305 | 3.3276 | 2.776 | 665.3926 | 35.5878 | 607.9819 | 607.2639 | 192.3542 | 674.5924 | 0.59517 | 0.19716 | 0.32584 | 8.9391 | 0.98447 | 34.2401 | 1.3477 | 3.0193 | 327.5462 | 293.4959 | 0.10828 | 2.2407 | 578.2519 | 8.0621 | -0.26643 | 35.5878 | 34.7873 | -3.0979 | -7.3971 | -0.31143 | 15.8054 | 4.1458 | -3.609 | 1.2738 | 71.1106 | 34.4417 | 69.0212 | 11.5968 | 11.3239 | 3.348 | 2.7284 | 680.4869 | 36.3785 | 608.6856 | 563.6625 | 192.7237 | 684.9946 | 0.66745 | 0.21387 | 0.35321 | 8.7549 | 0.97956 | 34.2189 | 2.1596 | 3.1219 | 323.7379 | 295.7143 | 0.089555 | 2.2387 | 579.546 | 9.0646 | 1.011 | 36.3785 | 35.4528 | -2.9478 | -7.7908 | 0.18297 | 16.1992 | 4.1818 | 563.6625 | 1.0852 | 66.3658 | 34.4356 | 67.5969 | 11.2771 | 10.9045 | 3.3579 | 2.7637 | 678.3582 | 35.2923 | 607.7175 | 563.9883 | 0.60519 | 675.7138 | 0.60519 | 0.21062 | 0.43819 | 8.9027 | 0.9819 | 33.8023 | 1.4899 | 2.8738 | 355.5093 | 292.6682 | 0.19947 | 1.99 | 579.0499 | 8.5818 | -0.43613 | 35.2923 | 33.9995 | -2.8727 | -7.4966 | -0.85548 | 15.9049 | 3.9572 | 30.0438 | 35.0987 | 35.2698 | 34.855 | 527.9125 | 1.1384 | 1.2882 | 2.1652 | 7.543 | 8.2708 | 9.4112 | 25.8448 | 0.57014 | 977.6848 | 1.7546 | 4.7086 | 1.9755 | 3.0382 | 4.5049 | 5.0272 | 2.6653 | 6.7549 | 3.2131 | 4.3712 | 5.795 | 8.238 | 3.1395 | 8.4896 | 3.8013 | 5.0646 | 7.2386 | 9.8491 | 4.7945 | 9.0955 | 5.5774 | 6.9961 | 8.6532 | 10.5038 | 5.6354 | 5.0459 | 1.7546 | 10.5038 | 6.4046 | 6.9827 | 7.2459 | 1.5306 | 8.4083 | 6.8777 | 6.4694 | 76.9534 | 108.6446 | 64.7149 | 879.6099 | 884.6976 | 946.1147 | 2710.4231 | 2926.9327 |  | 2787.3765 | -0.047678 | -2.9728 | -7.553 | 1.008 | 2.3867 | -3.2513 | -3.4552 | -4.0791 | -4.7386 | -5.594 | -6.7459 | 0.665 | -3.609 | -3.955 | -4.3726 | -5.0995 | -6.1552 | -7.0582 | 1.2738 | -3.5394 | -3.8827 | -4.5578 | -4.9898 | -5.9043 | -6.8062 | 1.0852
19 / 1200 | 13.1572 | 10.9876 | 14.952 | 3.4 | -8.6121 | -3.7839 | 70.5241 | 34.4026 | 65.349 | 11.2767 | 11.2066 | 2.6734 | 2.2333 | 673.5056 | 35.2847 | 607.7076 | 607.4952 | 179.2821 | 684.6212 | 0.56013 | 0.21353 | 0.31539 | 7.4121 | 0.98248 | 34.1384 | 1.1462 | 2.6441 | 314.2914 | 292.6511 | 0.068823 | 1.9128 | 573.2117 | 8.5182 | 0.64377 | 35.2847 | 35.0464 | -8.482 | -12.3021 | -0.00025425 | 20.2979 | 3.69 | -8.7769 | -2.8311 | 77.6469 | 31.986 | 74.893 | 11.5746 | 11.386 | 2.7129 | 2.2056 | 693.2101 | 36.3011 | 608.6154 | 558.3292 | 180.1104 | 699.1538 | 0.64722 | 0.23776 | 0.35271 | 7.2847 | 0.97661 | 34.0704 | 2.2307 | 2.7356 | 313.367 | 295.499 | 0.064689 | 1.8899 | 574.9884 | 9.7369 | 3.6765 | 36.3011 | 35.6624 | -8.1389 | -12.5679 | 0.44544 | 20.5637 | 3.791 | 558.3292 | -3.7289 | 71.5708 | 34.0833 | 72.6255 | 11.22 | 11.0208 | 2.6985 | 2.2188 | 689.2994 | 35.0919 | 607.5356 | 558.477 | 0.57659 | 687.0353 | 0.57659 | 0.22666 | 0.42195 | 7.378 | 0.98155 | 33.7576 | 1.3342 | 2.5583 | 339.5327 | 292.1105 | 0.15049 | 1.7173 | 573.3901 | 8.7075 | 0.32027 | 35.0919 | 34.4036 | -8.2561 | -12.4364 | -0.48035 | 20.4322 | 3.4777 | 30.0419 | 35.0466 | 35.217 | 34.884 | 469.9334 | -0.69426 | -2.193 | 1.7882 | 7.7398 | 7.4835 | 8.764 | 24.9016 | 0.59914 | 978.2452 | 0.70946 | 5.0528 | 0.019951 | 2.3315 | 4.9669 | 6.0406 | 2.5306 | 8.4823 | 2.4845 | 4.0984 | 7.3697 | 10.3327 | 2.0681 | 9.7917 | 2.6685 | 4.2185 | 8.5758 | 11.1919 | 3.4951 | 9.1975 | 4.3295 | 6.0147 | 9.1012 | 10.6944 | 5.6569 | 5.0098 | 0.019951 | 11.1919 | 8.434 | 9.6765 | 6.9758 | -0.36636 | 7.9958 | 8.3621 | 5.52 | 77.1076 | 47.9576 | 64.7612 | 867.8575 | 870.5099 | 935.9122 | 2674.2791 | 2830.2203 |  | 2751.3867 | -0.027833 | -8.2923 | -12.3999 | -3.448 | 2.0599 | -8.6121 | -8.7993 | -9.3298 | -9.9332 | -10.6153 | -11.6634 | -3.7839 | -8.7769 | -9.122 | -9.5599 | -10.2345 | -11.1444 | -11.9627 | -2.8311 | -8.9587 | -9.2137 | -9.8544 | -10.2101 | -10.9719 | -11.794 | -3.7289
19 / 1800 | 12.7706 | 14.3663 | 13.8581 | 3.4 | -2.3079 | 1.46 | 65.1604 | 35.1273 | 61.048 | 11.4008 | 11.1209 | 3.4597 | 2.8791 | 663.8828 | 35.7148 | 608.0951 | 607.234 | 194.7358 | 672.7484 | 0.59628 | 0.19293 | 0.32497 | 9.2276 | 0.98465 | 34.3133 | 1.4015 | 3.0909 | 328.7728 | 293.8519 | 0.11115 | 2.3094 | 579.161 | 8.0195 | -0.37328 | 35.7148 | 34.754 | -2.1303 | -6.5594 | -0.41107 | 14.883 | 4.2516 | -2.6537 | 1.7281 | 69.438 | 34.87 | 67.477 | 11.652 | 11.3438 | 3.4778 | 2.8204 | 676.9896 | 36.5638 | 608.8496 | 564.4962 | 195.0524 | 681.2256 | 0.65203 | 0.2025 | 0.33724 | 9.019 | 0.98099 | 34.3624 | 2.2014 | 3.2203 | 319.6254 | 296.2357 | 0.074854 | 2.3455 | 579.9112 | 8.7648 | 0.65074 | 36.5638 | 35.5207 | -2.0021 | -7.0367 | 0.14238 | 15.3603 | 4.383 | 564.4962 | 1.919 | 65.4171 | 34.4582 | 66.6855 | 11.3027 | 10.8807 | 3.4896 | 2.869 | 676.3248 | 35.3797 | 607.7958 | 564.9342 | 0.60499 | 673.5984 | 0.60499 | 0.20669 | 0.44004 | 9.1966 | 0.98196 | 33.8505 | 1.5292 | 2.9272 | 357.9309 | 292.9132 | 0.2065 | 2.0418 | 580.0211 | 8.5594 | -0.5422 | 35.3797 | 33.916 | -1.913 | -6.6405 | -0.97803 | 14.9641 | 4.0668 | 30.0476 | 35.1651 | 35.3784 | 34.8941 | 534.4485 | 1.8359 | 2.0963 | 2.7994 | 7.6382 | 8.1446 | 9.188 | 25.9838 | 0.51591 | 975.0511 | 2.8628 | 5.6368 | 3.1915 | 3.8451 | 5.2237 | 5.5961 | 3.3341 | 7.0572 | 3.9644 | 4.731 | 6.2346 | 8.0357 | 3.8702 | 8.6504 | 4.5178 | 5.5047 | 7.3269 | 9.6831 | 5.5561 | 9.364 | 6.2294 | 7.5262 | 8.9208 | 10.5802 | 6.1435 | 5.6164 | 2.8628 | 10.5802 | 5.8023 | 6.0483 | 6.3885 | 2.2439 | 8.3236 | 6.0797 | 6.6968 | 77.0206 | 154.5175 | 64.7041 | 887.8211 | 878.2739 | 954.4057 | 2720.5015 | 2982.9874 |  | 2797.5221 | -0.062175 | -2.0151 | -6.7389 | 1.7024 | 2.4615 | -2.3079 | -2.5248 | -3.1676 | -3.8567 | -4.7495 | -5.9486 | 1.46 | -2.6537 | -3.007 | -3.4583 | -4.1991 | -5.3338 | -6.2912 | 1.7281 | -2.5736 | -2.9218 | -3.6304 | -4.0707 | -5.0319 | -5.9535 | 1.919
24 | 12.433 | 12.9577 | 13.7843 | 4.186 | -4.4779 | -0.61089 | 66.1074 | 34.508 | 61.7378 | 11.2308 | 11.016 | 3.1631 | 2.6251 | 665.9068 | 35.1325 | 607.574 | 606.905 | 189.2727 | 675.2949 | 0.57658 | 0.18884 | 0.28276 | 8.529 | 0.98454 | 34.2236 | 0.90891 | 3.0554 | 307.3493 | 292.2217 | 0.047994 | 2.2965 | 576.7474 | 8.0614 | -0.11849 | 35.1325 | 34.3895 | -4.3565 | -8.6723 | -0.64735 | 17.6103 | 4.1943 | -4.8463 | -0.025996 | 71.5106 | 33.3537 | 69.3133 | 11.4695 | 11.2218 | 3.1763 | 2.5729 | 681.4833 | 35.948 | 608.3029 | 562.1858 | 189.5113 | 686.2146 | 0.64713 | 0.20451 | 0.29848 | 8.3327 | 0.9795 | 34.2248 | 1.7232 | 3.1673 | 300.7255 | 294.506 | 0.023528 | 2.3075 | 578.0145 | 9.095 | 1.7486 | 35.948 | 35.1023 | -4.2596 | -9.121 | -0.11722 | 18.059 | 4.2747 | 562.1858 | 0.0019776 | 66.748 | 34.0246 | 67.9601 | 11.1583 | 10.834 | 3.1851 | 2.6187 | 679.4834 | 34.8832 | 607.3501 | 562.6207 | 0.59015 | 676.8849 | 0.59015 | 0.20526 | 0.40507 | 8.501 | 0.98124 | 33.7402 | 1.143 | 2.8762 | 340.7284 | 291.5245 | 0.15582 | 2.0138 | 577.85 | 8.7312 | -0.27282 | 34.8832 | 33.7517 | -4.1904 | -8.7293 | -0.99126 | 17.6673 | 3.9126 | 30.0338 | 35.0369 | 35.2195 | 34.743 | 438.7506 | -0.077998 | 0.2579 | 0.89899 | 7.8286 | 9.1862 | 9.7993 | 25.5707 | 0.60175 | 988.5725 | 1.5566 | 4.341 | 1.7155 | 2.7224 | 4.3297 | 4.8269 | 2.6819 | 7.4019 | 3.4188 | 4.3669 | 5.9346 | 8.432 | 3.1314 | 9.0537 | 4.0286 | 4.9034 | 7.5191 | 9.9218 | 4.6405 | 9.7447 | 6.5145 | 7.599 | 8.8295 | 10.3014 | 5.7465 | 4.8651 | 1.5566 | 10.3014 | 7.9066 | 8.9283 | 8.9003 | 0.35963 | 8.938 | 8.5784 | 6.6178 | 76.8944 | 75.3109 | 64.739 | 866.8549 | 861.437 | 950.5322 | 2678.8254 | 2860.9331 |  | 2755.7198 | -0.036773 | -4.2688 | -8.8277 | -0.21164 | 2.4698 | -4.4779 | -4.6878 | -5.2662 | -5.9318 | -6.7389 | -7.8897 | -0.61089 | -4.8463 | -5.2097 | -5.6533 | -6.3641 | -7.459 | -8.3076 | -0.025996 | -4.8167 | -5.1502 | -5.8017 | -6.2035 | -7.101 | -7.982 | 0.0019776
26 | 12.1234 | #NUM! | 12.2855 | 4.186 | -1.6208 | 1.9439 | 89.2102 | 53.7155 | 82.613 | 18.0347 | 17.9342 | 3.5473 | 2.9358 | 692.139 | 54.8819 | 623.1194 | 622.9574 | 196.2652 | 707.7044 | 0.74622 | 0.25714 | 0.39127 | 8.8363 | 0.98443 | 53.6549 | 1.227 | 2.905 | 363.2246 | 350.1543 | 0.047882 | 1.9134 | 579.7529 | 8.0589 | 0.91619 | 54.8819 | 54.6317 | -1.5116 | -6.1151 | -0.022536 | 15.3892 | 4.4943 | -2.0601 | 2.5306 | 96.5375 | 51.0435 | 93.2099 | 18.4067 | 18.1723 | 3.5481 | 2.8812 | 716.098 | 55.7997 | 623.7041 | 565.0294 | 196.2763 | 723.9143 | 0.86326 | 0.28621 | 0.46038 | 8.6316 | 0.97938 | 53.5342 | 2.2655 | 3.0183 | 366.0379 | 353.0055 | 0.048557 | 1.8546 | 581.0467 | 9.0838 | 4.1795 | 55.7997 | 55.2229 | -1.5072 | -6.5531 | 0.38215 | 15.8273 | 4.4931 | 565.0294 | 2.2467 | 91.278 | 51.837 | 93.2864 | 17.9241 | 17.6707 | 3.5676 | 2.9373 | 717.552 | 54.6065 | 622.941 | 565.5257 | 0.79441 | 712.8548 | 0.79441 | 0.27663 | 0.5311 | 8.8498 | 0.98297 | 53.2325 | 1.374 | 2.8749 | 392.5581 | 349.3021 | 0.15807 | 1.6618 | 580.2833 | 8.35 | 2.134 | 54.6065 | 53.971 | -1.3656 | -6.1033 | -0.63386 | 15.3775 | 4.1686 | 49.8873 | 54.6542 | 54.8408 | 54.6048 | 436.7203 | 1.319 | 1.8473 | 2.6952 | 8.4989 | 9.2209 | 10.1027 | 24.569 | 0.57338 | 984.99 | 3.0461 | 5.5575 | 3.1441 | 4.2846 | 5.3279 | 6.0184 | 3.9271 | 7.7908 | 4.4667 | 5.6117 | 7.155 | 9.204 | 4.2985 | 9.3041 | 5.0153 | 6.1693 | 8.2669 | 10.5557 | 5.6135 | 9.987 | 7.2489 | 8.7145 | 9.4538 | 10.8529 | 6.7089 | 6.0939 | 3.0443 | 10.8529 | 7.18 | 7.3736 | 7.4076 | 1.9538 | 9.2742 | 7.3204 | 5.4298 | 76.9955 | 74.3593 | 64.7922 | 1205.0817 | 1220.5263 | 1327.9369 | 3753.5381 | 3941.2768 |  | 3830.5336 | -0.031444 | -1.4615 | -6.2518 | 2.2404 | 1.4275 | -1.655 | -2.0878 | -2.7347 | -3.5123 | -4.3678 | -5.5477 | 1.9262 | -2.0955 | -2.6589 | -3.1717 | -3.9794 | -5.0568 | -5.9436 | 2.5032 | -1.9707 | -2.517 | -3.2473 | -3.7334 | -4.629 | -5.5384 | 2.2211
27 | 9.8011 | 10.799 | 11.8698 | 4.186 | -0.89615 | 2.8766 | 61.575 | 33.0607 | 57.5032 | 11.125 | 10.0167 | 3.7276 | 2.9847 | 657.1402 | 34.7683 | 607.2469 | 603.5988 | 199.4409 | 665.8932 | 0.56192 | 0.21056 | 0.44325 | 9.582 | 0.98177 | 33.8841 | 0.88421 | 2.6691 | 378.5679 | 291.2033 | 0.27641 | 1.9412 | 581.1687 | 8.5891 | -2.2691 | 34.7683 | 30.7916 | -0.2254 | -5.7124 | -3.9365 | 14.7447 | 4.8163 | -0.58573 | 2.5075 | 61.1011 | 33.4429 | 59.5052 | 11.284 | 10.1798 | 3.7565 | 2.9738 | 660.9324 | 35.3161 | 607.739 | 565.8624 | 199.9346 | 664.3714 | 0.54086 | 0.20392 | 0.50084 | 9.551 | 0.98318 | 33.8019 | 1.5142 | 2.6522 | 383.1997 | 292.7348 | 0.28717 | 1.8848 | 580.5663 | 8.3066 | -2.0469 | 35.3161 | 31.3961 | -0.026349 | -5.7992 | -3.3027 | 14.8314 | 5.2134 | 565.8624 | 2.0389 | 61.2432 | 34.018 | 61.5105 | 11.2834 | 10.6251 | 3.5416 | 2.8943 | 665.2543 | 35.3143 | 607.7374 | 565.1637 | 0.52902 | 664.6788 | 0.52902 | 0.18307 | 0.42823 | 9.2899 | 0.98239 | 34.174 | 1.1403 | 2.8896 | 354.1998 | 292.7296 | 0.19514 | 2.0987 | 580.1121 | 8.4717 | -1.007 | 35.3143 | 33.011 | -1.536 | -6.4329 | -2.1065 | 15.4651 | 4.5872 | 30.0162 | 34.7281 | 34.6988 | 35.1174 | 406.0419 | 1.5998 | 2.2799 | 2.9439 | 7.8934 | 8.9975 | 10.206 | 24.3319 | 0.58718 | 974.6441 | 2.9655 | 5.6893 | 3.3778 | 4.3923 | 5.2854 | 6.0417 | 3.6447 | 7.865 | 4.5595 | 5.3235 | 6.5359 | 8.4699 | 4.048 | 9.2781 | 5.0727 | 7.1243 | 7.5965 | 10.5625 | 5.5033 | 9.8693 | 6.8045 | 7.647 | 8.8995 | 10.8977 | 6.5606 | 6.2888 | 2.9655 | 10.8977 | 6.2936 | 6.7176 | 7.2621 | 2.2746 | 9.0323 | 6.7577 | 5.9246 | 76.9054 | 74.9687 | 64.8129 | 885.4687 | 800.8515 | 761.3304 | 2447.6526 | 2622.0275 |  | 2524.5579 | -0.037171 | -0.59592 | -5.98 | 2.4743 | 2.4204 | -0.89615 | -1.4153 | -2.1926 | -3.0519 | -4.0333 | -5.2692 | 2.8766 | -0.58573 | -1.3577 | -2.0135 | -2.899 | -4.1561 | -5.1711 | 2.5075 | -1.8457 | -2.3652 | -3.1415 | -3.685 | -4.7363 | -5.804 | 2.0389
28 | 10.507 | 11.818 | 12.1939 | 4.186 | 1.9014 | 4.7001 | 85.9959 | 52.9493 | 79.4006 | 17.8587 | 17.2299 | 4.1394 | 3.3567 | 685.0565 | 54.4432 | 622.8346 | 621.7707 | 206.322 | 700.6497 | 0.78269 | 0.31435 | 0.55636 | 10.0593 | 0.98666 | 53.2069 | 1.2363 | 2.4905 | 437.4597 | 348.7977 | 0.32354 | 1.4609 | 582.6854 | 7.5799 | -0.099459 | 54.4432 | 52.8499 | 2.5403 | -2.8798 | -1.4834 | 12.5129 | 4.7812 | 2.1743 | 4.823 | 85.6442 | 53.1413 | 83.1357 | 18.0297 | 17.2599 | 4.1702 | 3.3603 | 693.3971 | 54.8697 | 623.1117 | 569.0926 | 206.8158 | 699.3277 | 0.76652 | 0.32347 | 0.69254 | 10.0625 | 0.98616 | 52.8445 | 2.0252 | 2.3701 | 457.6969 | 350.1164 | 0.39407 | 1.2587 | 582.89 | 7.6786 | -0.21477 | 54.8697 | 52.9265 | 2.7375 | -2.8555 | -1.1901 | 12.4887 | 5.0299 | 569.0926 | 4.688 | 85.5678 | 53.076 | 85.7426 | 18.1056 | 17.6727 | 3.9833 | 3.2929 | 699.3401 | 55.0582 | 623.2331 | 568.546 | 0.74365 | 698.9269 | 0.74365 | 0.25812 | 0.55458 | 9.8289 | 0.98435 | 53.6907 | 1.3675 | 2.8812 | 406.046 | 350.7004 | 0.20308 | 1.7379 | 582.9616 | 8.0432 | 0.89988 | 55.0582 | 53.9759 | 1.5073 | -3.3552 | -1.0605 | 12.9883 | 4.4881 | 49.851 | 54.3333 | 54.1167 | 55.0364 | 398.2286 | 3.2301 | 3.8652 | 4.6734 | 8.6177 | 9.6333 | 10.6486 | 23.7119 | 0.54664 | 970.5537 | 5.3332 | 7.7408 | 5.7775 | 6.5609 | 7.3693 | 8.0721 | 5.6592 | 9.4384 | 6.6029 | 7.1191 | 8.1788 | 9.5154 | 6.0272 | 10.6417 | 6.9677 | 8.3896 | 9.0573 | 11.4376 | 7.2345 | 11.1821 | 8.5059 | 9.2462 | 10.2233 | 11.9313 | 8.2588 | 8.1254 | 5.3332 | 11.9313 | 5.3876 | 5.7681 | 5.9752 | 3.9229 | 9.6332 | 5.7103 | 4.4576 | 77.1512 | 74.5772 | 64.7834 | 1300.6684 | 1207.9759 | 1110.5316 | 3619.1782 | 3800.8651 |  | 3696.3294 | -0.027503 | 2.2617 | -3.0286 | 4.7371 | 1.2316 | 1.9014 | 1.2381 | 0.46123 | -0.42979 | -1.3663 | -2.5275 | 4.7001 | 2.1743 | 1.2897 | 0.68771 | -0.25047 | -1.4024 | -2.3983 | 4.823 | 1.1329 | 0.45924 | -0.34329 | -0.92815 | -1.9618 | -2.95 | 4.688
34 | 10.2683 | 12.4014 | 11.8122 | 4.186 | -1.974 | 1.2847 | 67.9132 | 38.2486 | 62.9373 | 12.5157 | 11.6935 | 3.5542 | 2.8377 | 664.4123 | 39.3931 | 611.315 | 608.9722 | 196.3872 | 675.3413 | 0.5794 | 0.23206 | 0.46574 | 9.0605 | 0.98381 | 38.6111 | 0.78198 | 2.4971 | 388.5128 | 304.2458 | 0.27443 | 1.7249 | 579.0562 | 8.1892 | -1.5458 | 39.3931 | 36.7027 | -1.4622 | -6.9046 | -2.7792 | 15.3202 | 4.9306 | -2.6771 | 0.64715 | 69.1326 | 39.2702 | 66.9729 | 12.8644 | 12.2985 | 3.4462 | 2.7471 | 672.1985 | 40.4975 | 612.2559 | 563.8167 | 194.4597 | 676.9611 | 0.56561 | 0.20888 | 0.45478 | 8.7581 | 0.98332 | 38.9143 | 1.5832 | 2.7078 | 362.3962 | 307.4005 | 0.18041 | 1.8876 | 578.366 | 8.2972 | -0.57666 | 40.4975 | 38.6935 | -2.2443 | -7.6501 | -1.1706 | 16.0657 | 4.973 | 563.8167 | 0.75317 | 68.0323 | 38.4834 | 67.8689 | 12.6582 | 12.1292 | 3.3572 | 2.7384 | 674.8094 | 39.8468 | 611.7031 | 563.7426 | 0.55409 | 675.1682 | 0.55409 | 0.20448 | 0.46268 | 8.7406 | 0.98246 | 38.8691 | 0.97769 | 2.7101 | 364.4481 | 305.5399 | 0.19242 | 1.8704 | 578.5939 | 8.4707 | -0.33924 | 39.8468 | 38.1442 | -2.8909 | -7.7175 | -1.7235 | 16.1331 | 4.6716 | 34.9562 | 39.482 | 39.8641 | 39.8677 | 395.4531 | 0.073821 | 1.0016 | 2.2446 | 6.4196 | 8.2841 | 10.543 | 24.0664 | 0.58571 | 987.3658 | 2.074 | 5.101 | 2.6019 | 4.1706 | 4.5632 | 5.7432 | 2.7451 | 7.2234 | 3.978 | 5.3374 | 5.9663 | 8.6449 | 2.8019 | 8.7076 | 4.36 | 7.1963 | 6.3786 | 10.4975 | 3.8435 | 9.1933 | 6.0009 | 7.5068 | 7.227 | 10.7027 | 5.9402 | 5.8471 | 2.074 | 10.7027 | 6.3458 | 7.2825 | 8.2985 | 1.1067 | 8.4156 | 7.3089 | 5.483 | 80.2864 | 75.1732 | 64.9267 | 971.7449 | 888.915 | 831.7502 | 2692.4065 | 2871.2752 |  | 2772.6929 | -0.034332 | -2.1991 | -7.4161 | 0.895 | 2.0363 | -1.974 | -2.5763 | -3.2853 | -4.1406 | -5.0192 | -6.2824 | 1.2847 | -2.6771 | -3.3622 | -3.9013 | -4.7681 | -5.9082 | -6.9117 | 0.64715 | -3.0459 | -3.651 | -4.4044 | -4.9729 | -5.9548 | -7.0265 | 0.75317
35 | 10.3771 | 12.4883 | 12.2033 | 4.186 | -3.4974 | -0.016044 | 62.7217 | 33.3274 | 58.2555 | 11.0407 | 10.1975 | 3.3483 | 2.6672 | 659.0343 | 34.4756 | 606.9829 | 604.2237 | 192.704 | 668.6138 | 0.53585 | 0.21155 | 0.42524 | 8.6993 | 0.98336 | 33.7456 | 0.72997 | 2.5337 | 367.6972 | 290.3866 | 0.24419 | 1.8263 | 577.5885 | 8.2952 | -1.8653 | 34.4756 | 31.4622 | -2.9571 | -8.3112 | -3.0988 | 16.0507 | 4.8139 | -4.1767 | -0.77723 | 64.001 | 34.4094 | 62.035 | 11.3484 | 10.8002 | 3.2489 | 2.5804 | 666.1778 | 35.5368 | 607.9365 | 562.2619 | 190.8678 | 670.4123 | 0.52472 | 0.19009 | 0.39495 | 8.4133 | 0.98349 | 34.089 | 1.4477 | 2.7606 | 337.5167 | 293.3526 | 0.1404 | 2.0094 | 576.6759 | 8.2756 | -0.77747 | 35.5368 | 33.6319 | -3.7057 | -9.0528 | -1.3385 | 16.7922 | 4.8761 | 562.2619 | -0.41887 | 63.2385 | 33.8158 | 63.1059 | 11.161 | 10.6501 | 3.1525 | 2.5728 | 669.0659 | 34.893 | 607.3592 | 562.1942 | 0.51964 | 669.3504 | 0.51964 | 0.19202 | 0.42121 | 8.3883 | 0.98144 | 33.9399 | 0.95311 | 2.7063 | 346.2373 | 291.5517 | 0.17317 | 1.9382 | 577.3386 | 8.6953 | -0.71581 | 34.893 | 33.1 | -4.4307 | -9.1141 | -1.7718 | 16.8536 | 4.492 | 29.9968 | 34.561 | 34.9705 | 34.8718 | 397.7991 | -1.0145 | -0.080025 | 1.2219 | 5.9091 | 7.602 | 9.7073 | 24.2203 | 0.59084 | 987.2409 | 0.97833 | 4.583 | 1.3422 | 3.4893 | 4.0819 | 5.6236 | 1.9265 | 7.0918 | 2.9924 | 4.6553 | 5.7694 | 8.7447 | 1.7506 | 8.4972 | 3.2761 | 6.518 | 6.158 | 10.5524 | 3.0308 | 8.6862 | 5.1038 | 6.6812 | 6.9551 | 10.2592 | 5.3645 | 5.3637 | 0.97833 | 10.5524 | 6.9236 | 7.682 | 8.4854 | 0.042473 | 7.7395 | 7.697 | 5.7739 | 80.2874 | 75.018 | 64.8956 | 877.7726 | 808.9881 | 756.1159 | 2442.8722 | 2620.6593 |  | 2523.1596 | -0.037201 | -3.6978 | -8.8138 | -0.40405 | 2.3633 | -3.4974 | -4.0206 | -4.7117 | -5.5319 | -6.3911 | -7.6377 | -0.016044 | -4.1767 | -4.7932 | -5.3072 | -6.1687 | -7.2895 | -8.284 | -0.77723 | -4.6221 | -5.1505 | -5.8779 | -6.4156 | -7.3712 | -8.4056 | -0.41887
Note on W14: Author: still lower than select

## input
Patm | 0.9831 | bar |  | Rice factor | 0.85
cpH2O |  | kJ/kgK |  | Suction Superheat COEFF | 5 | K
ZB09KAU-TFD
| C0 | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | C9
Capacity | 4.6469 | 0.16581 | -0.029031 | 0.002086 | -0.00083935 | -0.00020769 | 8.7756e-06 | -1.1029e-05 | -4.9038e-06 | 9.985e-07
Power Input | 0.31404 | -0.007295 | 0.01213 | -0.00013701 | 0.00017331 | -1.0595e-15 | 4.575e-18 | 5.8932e-07 | -1.1597e-07 | 1.3949e-06
Current | 1.9068 | 0.0015636 | 0.00046268 | -1.1846e-06 | -8.062e-05 | 9.1588e-05 | 4.0449e-07 | 2.6203e-06 | 4.6587e-06 | 9.1761e-07
Mass Flow | 12.1617 | 0.39532 | 0.0058752 | 0.0041954 | 0.00060096 | -0.0005133 | 1.5542e-05 | 4.6705e-06 | -9.7088e-06 | 1.6965e-06
X = C0 + C1*S + C2*D + C3*S^2 + C4*S*D + C5*D^2 + C6*S^3 + C7*D*S^2 +C8*S*D^2 + C9*D^3
X = Capacity kW; Power Input kW; Current A; Mass Flow g/s
S = Evaporating Temperature, °C
D = Cond. Temp., °C

## new table
Test # | LMTD C1 [K] | LMTD C2 [K] | LMTD C3 [K] | cpw | Temperatures - C1 Evap in (deg C) | Temperatures - C1 Evap out (deg C) | Temperatures - C1 discharge (deg C) | Temperatures - C1 liquid / cond out (deg C) | Temperatures - C1 condensor in (deg C) | Pressures - C1 discharge pressure (bar) | Pressures - C1 liquid line pressure (bar) | Pressures - C1 evap in pressure (bar) | Pressures - C1 evap out pressure (bar) | h cond in C1 [kJ/kg] | TVAP,SAT HP C1 [°C] | hVAP,SAT HP C1 [kJ/kg] | hVAP,SAT LP C1 [kJ/kg] | hLIQ,SAT LP C1 [kJ/kg] | hDISCHARGE C1 [kJ/kg] | Q_DESH C1 [kW] | % DESH C1 | xEVAP,IN C1 | massflow R290 C1 (coeffs) [g/s] | v_MAP/v_REAL | TW,PINCH C1 [°C] | DTPINCH C1 [°C] | Q_cond_water C1 [kW] | h_cond_out C1 [kJ/kg] | h_LIQ,SAT HP C1 [kJ/kg] | xCOND,OUT C1 | Qevap C1 [kW] | h_evap,out C1 [kJ/kg] | DTSH C1 | DTSC C1 | Tsat C1 discharge [°C] | Tsat C1 liquid line Tcond [°C] | Tsat C1 evap in [°C] | Tsat C1 evap out (dew) Tevap [°C] | DT = TCOND - Tw,out C1 | DT = TAIR,IN - TEVAP(dew) C1 | DTGLIDE = TREF,IN - TEVAP(dew) C1 | Temperatures - C2 Evap in (deg C) | Temperatures - C2 Evap out (deg C) | Temperatures - C2 discharge (deg C) | Temperatures - C2 liquid (deg C) | Temperatures - C2 condensor in (deg C) | Pressures - C2 discharge pressure (bar) | Pressures - C2 liquid line pressure (bar) | Pressures - C2 evap in pressure (bar) | Pressures - C2 evap out pressure (bar) | h cond in C2 [kJ/kg] | TVAP,SAT HP C2 [°C] | hVAP,SAT HP C2 [kJ/kg] | hVAP,SAT LP C2 [kJ/kg] | hLIQ,SAT LP C2 [kJ/kg] | hDISCHARGE C2 [kJ/kg] | Q_DESH C2 [kW] | % DESH C2 | xEVAP,IN C2 | massflow R290 C2 (coeffs) [g/s] | v_MAP/v_REAL | TW,PINCH C2 [°C] | DTPINCH C2 [°C] | Q_cond_water C2 [kW] | h_cond_out C2 [kJ/kg] | h_LIQ,SAT HP C2 [kJ/kg] | xCOND,OUT C2 | Qevap C2 [kW] | h_evap,out C2 [kJ/kg] | DTSH C2 | DTSC C2 | Tsat C2 discharge [°C] | Tsat C2 liquid line [°C] | Tsat C2 evap in [°C] | Tsat C2 evap out (dew) [°C] | DT = TCOND - Tw,out C2 | DT = TAIR,IN - TEVAP(dew) C2 | DTGLIDE = TREF,IN - TEVAP(dew) C2 | Temperatures - C3 Evap in (deg C) | Temperatures - C3 Evap out (deg C) | Temperatures - C3 discharge (deg C) | Temperatures - C3 liquid (deg C) | Temperatures - C3 condensor in (deg C) | Pressures - C3 discharge pressure (bar) | Pressures - C3 liquid line pressure (bar) | Pressures - C3 evap in pressure (bar) | Pressures - C3 evap out pressure (bar) | h cond in C3 [kJ/kg] | TVAP,SAT C3 [°C] | hVAP,SAT HP C3 [kJ/kg] | hVAP,SAT LP C3 [kJ/kg] | hLIQ,SAT LP C3 [kJ/kg] | hDISCHARGE C3 [kJ/kg] | Q_DESH C3 [kW] | % DESH C3 | xEVAP,IN C3 | massflow R290 C3 (coeffs) [g/s] | v_MAP/v_REAL | TW,PINCH C3 [°C] | DTPINCH C3 [°C] | Qcond,water C3 [kW] | hcond,out C3 [kJ/kg] | h_LIQ,SAT HP C3 [kJ/kg] | xCOND,OUT C3 | Qevap C3 [kW] | h_evap,out C3 [kJ/kg] | DTSH C3 | DTSC C3 | Tsat C3 discharge [°C] | Tsat C3 liquid line [°C] | Tsat C3 evap in [°C] | Tsat C3 evap out (dew) [°C] | DT = TCOND - Tw,out C3 | DT = TAIR,IN - TEVAP(dew) C3 | DTGLIDE = TREF,IN - TEVAP(dew) C3 | Temperatures - water in (deg C) | Temperatures - C1 water out (deg C) | Temperatures - C2 water out (deg C) | Temperatures - C3 water out (deg C) | Water mass flow (g/s) | Temperatures - air out left (deg C) | Temperatures - air out mid (deg C) | Temperatures - air out right (deg C) | Temperatures - air in left (deg C) | Temperatures - air in mid (deg C) | Temperatures - air in right (deg C) | Temperatures - ambient temp (deg C) | Relative Humidity | Absolute Pressure (Pa) | Temperatures - BL 1.1 (deg C) | Temperatures - BL 1.2 (deg C) | Temperatures - BL 1.3 (deg C) | Temperatures - BL 1.4 (deg C) | Temperatures - BL 1.5 (deg C) | Temperatures - BL 1.6 (deg C) | Temperatures - BL 2.1 (deg C) | Temperatures - BL 2.2 (deg C) | Temperatures - BL 2.3 (deg C) | Temperatures - BL 2.4 (deg C) | Temperatures - BL 2.5 (deg C) | Temperatures - BL 2.6 (deg C) | Temperatures - BL 3.1 (deg C) | Temperatures - BL 3.2 (deg C) | Temperatures - BL 3.3 (deg C) | Temperatures - BL 3.4 (deg C) | Temperatures - BL 3.5 (deg C) | Temperatures - BL 3.6 (deg C) | Temperatures - BL 4.1 (deg C) | Temperatures - BL 4.2 (deg C) | Temperatures - BL 4.3 (deg C) | Temperatures - BL 4.4 (deg C) | Temperatures - BL 4.5 (deg C) | Temperatures - BL 4.6 (deg C) | T_BL avg | T_BL_median | T_BL min | T_BL max | DT air in/out LEFT | DT air in/out MID | DT air in/out RIGHT | Temperatures - air out AVG (deg C) | Temperatures - air in AVG (deg C) | DTAIR IN - OUT | Qevap,TOT | P-E1[W] | P-E2[W] | P-E3[W] | P-E4[W] | P-E5[W] | P-E6[W] | P-SigA[W] | Total P from Chamber [W] | Wh | P1+PsigA | Meas. Difference | T_SAT_ev_in AVG | T_SAT_ev_out AVG | T_su AVG | DT cond out | DT cond in | Qev1 Select | Qev2 Select | Qev3 Select | COP compr | Temperatures - C1 Evap in (deg C) | Temperatures - C1 Evap 1. pass (deg C) | Temperatures - C1 Evap 2. pass (deg C) | Temperatures - C1 Evap 3. pass (deg C) | Temperatures - C1 Evap 4. pass (deg C) | Temperatures - C1 Evap 5. pass (deg C) | Temperatures - C1 Evap out (deg C) | Temperatures - C2 Evap in (deg C) | Temperatures - C2 Evap 1. pass (deg C) | Temperatures - C2 Evap 2. pass (deg C) | Temperatures - C2 Evap 3. pass (deg C) | Temperatures - C2 Evap 4. pass (deg C) | Temperatures - C2 Evap 5. pass (deg C) | Temperatures - C2 Evap out (deg C) | Temperatures - C3 Evap in (deg C) | Temperatures - C3 Evap 1. pass (deg C) | Temperatures - C3 Evap 2. pass (deg C) | Temperatures - C3 Evap 3. pass (deg C) | Temperatures - C3 Evap 4. pass (deg C) | Temperatures - C3 Evap 5. pass (deg C) | Temperatures - C3 Evap out (deg C)
5 | 16.1825 | 17.3286 | 16.4772 | 3.4 | -4.9773 | 6.08 | 72.1586 | 34.7922 | 69.402 | 11.2106 | 10.7939 | 3.1293 | 2.5693 | 682.4246 | 35.0637 | 607.5125 | 606.1981 | 188.6872 | 688.3367 | 0.65828 | 0.23624 | 0.36313 | 8.148 | 0.95086 | 32.9703 | 2.0934 | 2.7875 | 340.3036 | 292.029 | 0.15301 | 2.0242 | 588.6995 | 15.21 | -1.182 | 35.0637 | 33.6102 | -4.5931 | -9.13 | -0.42875 | 19.5837 | 4.1527 | -3.4159 | 4.1459 | 72.4441 | 35.7307 | 70.8625 | 11.6058 | 11.1436 | 3.3121 | 2.773 | 684.4359 | 36.4089 | 608.7125 | 564.0681 | 192.0684 | 687.8479 | 0.69615 | 0.21695 | 0.34293 | 8.7978 | 0.96748 | 33.6108 | 2.7981 | 3.2095 | 319.6465 | 295.8001 | 0.076202 | 2.3301 | 584.3998 | 11.5699 | -0.89866 | 36.4089 | 34.832 | -3.2144 | -7.4241 | 0.05448 | 17.8777 | 4.0082 | 564.0681 | 5.1594 | 69.7467 | 34.564 | 71.2947 | 11.2582 | 10.8974 | 3.1884 | 2.6586 | 686.3505 | 35.2276 | 607.6595 | 563.0192 | 0.63571 | 683.0279 | 0.63571 | 0.22478 | 0.43204 | 8.4371 | 0.95841 | 32.949 | 2.2786 | 2.829 | 351.0462 | 292.4872 | 0.1858 | 1.9886 | 586.6907 | 13.5311 | -0.58956 | 35.2276 | 33.9744 | -4.1428 | -8.3717 | -0.13705 | 18.8254 | 3.9773 | 29.1568 | 34.0389 | 34.7775 | 34.1115 | 504.0316 | 2.0152 | 1.2652 | 1.0838 | 8.9238 | 10.8425 | 11.5947 | 25.4836 | 0.57934 | 990.9201 | 3.4961 | 5.474 | 3.0583 | 2.6833 | 5.5865 | 5.2531 | 4.1214 | 7.3754 | 4.099 | 4.78 | 7.2697 | 7.8689 | 4.744 | 9.1183 | 4.8504 | 5.023 | 8.9728 | 9.551 | 6.6041 | 10.0434 | 6.0647 | 6.8242 | 9.5943 | 10.2283 | 6.3618 | 5.8256 | 2.6833 | 10.2283 | 6.9086 | 9.5773 | 10.511 | 1.4547 | 10.4537 | 8.999 | 5.7422 | 147.6308 | 69.9419 | 64.6957 | 868.0502 | 868.1035 | 937.5509 | 2673.7077 | 2841.479 |  | 2821.3385 | -0.0070863 | -3.9834 | -8.3033 | 5.1284 |  |  | 2.3046 | 2.476 | 2.3854 | 2.1473 | -4.9773 | -12927.0378 | -5.8451 | -6.2632 | -7.3248 | -0.89133 | 6.08 | -3.4159 | -3.5978 | -4.0382 | -4.7596 | -5.4755 | -5.4138 | 4.1459 | -4.3944 | -3.9774 | -5.1822 | -5.8073 | -5.8846 | -4.5441 | 5.1594
4 | 14.341 | 16.6122 | 14.2073 | 3.3561 | 0.82293 | 7.7446 | 88.8698 | 53.5204 | 85.4 | 17.8478 | 17.206 | 3.8856 | 3.2435 | 699.2792 | 54.416 | 622.8168 | 621.7291 | 202.1293 | 707.427 | 0.8116 | 0.33623 | 0.58508 | 9.5922 | 0.96758 | 51.94 | 2.4761 | 2.4139 | 447.629 | 348.7135 | 0.36087 | 1.3528 | 588.6623 | 11.4638 | -0.73156 | 54.416 | 52.7888 | 0.85799 | -3.7192 | -0.5505 | 14.4264 | 4.5421 | 1.7814 | 4.9244 | 91.0022 | 55.0357 | 89.0246 | 18.438 | 17.9097 | 4.0628 | 3.3773 | 706.1479 | 55.8766 | 623.7526 | 569.2359 | 205.0754 | 710.817 | 0.8755 | 0.29278 | 0.55936 | 10.0559 | 0.9863 | 52.8581 | 3.0184 | 2.9903 | 408.7723 | 353.2449 | 0.20527 | 1.7519 | 582.9903 | 7.6495 | -0.46494 | 55.8766 | 54.5707 | 2.0412 | -2.7251 | 0.13179 | 13.4323 | 4.5065 | 569.2359 | 6.1886 | 86.1075 | 52.7792 | 88.4649 | 17.9376 | 17.4384 | 4.0281 | 3.3435 | 706.2283 | 54.6404 | 622.9631 | 568.964 | 0.7724 | 700.6861 | 0.7724 | 0.28149 | 0.61903 | 9.9379 | 0.97873 | 52.3902 | 2.2501 | 2.744 | 430.1161 | 349.4067 | 0.29504 | 1.5434 | 585.4187 | 9.1624 | 0.60373 | 54.6404 | 53.3829 | 1.812 | -2.9738 | -0.58616 | 13.681 | 4.5398 | 48.7337 | 53.3393 | 54.4389 | 53.969 | 468.5502 | 4.2998 | 4.2636 | 4.2387 | 9.3743 | 11.1327 | 11.6146 | 23.9108 | 0.60306 | 985.2164 | 3.6431 | 5.9402 | 2.7741 | 3.0827 | 5.9538 | 6.0047 | 4.5773 | 7.4755 | 3.9234 | 4.448 | 7.3623 | 7.9665 | 4.6115 | 8.7561 | 4.2311 | 4.1609 | 8.697 | 9.0338 | 5.982 | 9.6647 | 5.1071 | 6.0505 | 9.4512 | 9.5022 | 6.1833 | 5.9679 | 2.7741 | 9.6647 | 5.0746 | 6.8691 | 7.376 | 4.2673 | 10.7072 | 6.4399 | 4.6481 | 147.0164 | 69.3007 | 64.6899 | 1246.0612 | 1204.0669 | 1334.6496 | 3784.7826 | 3959.0541 |  | 3931.7991 | -0.0068841 | 1.5704 | -4.943 | 6.2859 |  |  | 2.2384 | 2.3029 | 2.3094 | 1.2281
18 | 13.2635 | 12.4893 | 14.5119 | 3.4 | -5.9735 | -1.8313 | 68.0399 | 34.8894 | 63.3606 | 11.3157 | 11.1903 | 2.9826 | 2.4865 | 669.1279 | 35.4224 | 607.8331 | 607.4484 | 185.7866 | 679.1892 | 0.57779 | 0.20474 | 0.32022 | 8.131 | 0.98464 | 34.1927 | 1.2298 | 2.8282 | 320.8157 | 293.0339 | 0.088281 | 2.0683 | 575.2981 | 8.0539 | 0.10354 | 35.4224 | 34.9929 | -5.7861 | -9.8852 | -0.083318 | 18.3984 | 3.9117 | -6.2694 | -0.91827 | 74.1792 | 32.8761 | 71.8216 | 11.5702 | 11.3424 | 3.0091 | 2.4419 | 686.5988 | 36.2879 | 608.6047 | 560.8945 | 186.3021 | 691.6826 | 0.6572 | 0.22446 | 0.34849 | 7.9523 | 0.97828 | 34.1608 | 2.1271 | 2.9313 | 316.7972 | 295.4608 | 0.069087 | 2.0647 | 577.0955 | 9.3624 | 2.6393 | 36.2879 | 35.5153 | -5.5745 | -10.2807 | 0.2566 | 18.794 | 4.0113 | 560.8945 | -1.6297 | 68.0242 | 34.4176 | 69.2098 | 11.2707 | 11.0029 | 3.0025 | 2.4494 | 681.8361 | 35.2692 | 607.6962 | 560.9732 | 0.57247 | 679.2902 | 0.57247 | 0.20876 | 0.40788 | 8.0233 | 0.98205 | 33.8714 | 1.3977 | 2.7452 | 339.0316 | 292.6044 | 0.14739 | 1.8981 | 575.8345 | 8.5806 | -0.074455 | 35.2692 | 34.3431 | -5.6251 | -10.2103 | -0.58478 | 18.7236 | 3.8898 | 30.0378 | 35.0762 | 35.2587 | 34.9279 | 497.6219 | -1.0207 | -1.1343 | 0.33825 | 7.5111 | 8.3974 | 9.6313 | 25.5895 | 0.56294 | 976.9779 | 0.47356 | 3.8031 | 0.40121 | 2.1348 | 3.6687 | 4.6986 | 2.0457 | 6.9203 | 2.4122 | 3.9674 | 5.6719 | 8.8986 | 2.4287 | 8.7661 | 3.062 | 4.6555 | 7.4454 | 10.3627 | 3.9964 | 9.1191 | 4.9975 | 6.5761 | 8.611 | 10.7077 | 5.2427 | 4.6771 | 0.40121 | 10.7077 | 8.5317 | 9.5317 | 9.293 | -0.60557 | 8.5133 | 9.1188 | 6.031 | 77.1202 | 73.0477 | 64.7503 | 880.1875 | 868.4488 | 944.8696 | 2693.5058 | 2874.748 |  | 2770.8779 | -0.036122 | -5.6619 | -10.1058 | -1.4597 |  |  | 2.2579 | 2.1924 | 2.2398 | 2.2376 | -5.9735 | -6.1848 | -6.7305 | -7.3573 | -8.1206 | -9.2381 | -1.8313 | -6.2694 | -6.6217 | -7.0299 | -7.7635 | -8.751 | -9.6175 | -0.91827 | -6.3205 | -6.649 | -7.3125 | -7.7362 | -8.5867 | -9.481 | -1.6297
19 / 1600 | 12.926 | 14.3761 | 14.1091 | 3.4 | -3.2513 | 0.665 | 65.9647 | 35.0537 | 61.6928 | 11.3635 | 11.1305 | 3.3276 | 2.776 | 665.3926 | 35.5878 | 607.9819 | 607.2639 | 192.3542 | 674.5924 | 0.59517 | 0.19716 | 0.32584 | 8.9391 | 0.98447 | 34.2401 | 1.3477 | 3.0193 | 327.5462 | 293.4959 | 0.10828 | 2.2407 | 578.2519 | 8.0621 | -0.26643 | 35.5878 | 34.7873 | -3.0979 | -7.3971 | -0.31143 | 15.8054 | 4.1458 | -3.609 | 1.2738 | 71.1106 | 34.4417 | 69.0212 | 11.5968 | 11.3239 | 3.348 | 2.7284 | 680.4869 | 36.3785 | 608.6856 | 563.6625 | 192.7237 | 684.9946 | 0.66745 | 0.21387 | 0.35321 | 8.7549 | 0.97956 | 34.2189 | 2.1596 | 3.1219 | 323.7379 | 295.7143 | 0.089555 | 2.2387 | 579.546 | 9.0646 | 1.011 | 36.3785 | 35.4528 | -2.9478 | -7.7908 | 0.18297 | 16.1992 | 4.1818 | 563.6625 | 1.0852 | 66.3658 | 34.4356 | 67.5969 | 11.2771 | 10.9045 | 3.3579 | 2.7637 | 678.3582 | 35.2923 | 607.7175 | 563.9883 | 0.60519 | 675.7138 | 0.60519 | 0.21062 | 0.43819 | 8.9027 | 0.9819 | 33.8023 | 1.4899 | 2.8738 | 355.5093 | 292.6682 | 0.19947 | 1.99 | 579.0499 | 8.5818 | -0.43613 | 35.2923 | 33.9995 | -2.8727 | -7.4966 | -0.85548 | 15.9049 | 3.9572 | 30.0438 | 35.0987 | 35.2698 | 34.855 | 527.9125 | 1.1384 | 1.2882 | 2.1652 | 7.543 | 8.2708 | 9.4112 | 25.8448 | 0.57014 | 977.6848 | 1.7546 | 4.7086 | 1.9755 | 3.0382 | 4.5049 | 5.0272 | 2.6653 | 6.7549 | 3.2131 | 4.3712 | 5.795 | 8.238 | 3.1395 | 8.4896 | 3.8013 | 5.0646 | 7.2386 | 9.8491 | 4.7945 | 9.0955 | 5.5774 | 6.9961 | 8.6532 | 10.5038 | 5.6354 | 5.0459 | 1.7546 | 10.5038 | 6.4046 | 6.9827 | 7.2459 | 1.5306 | 8.4083 | 6.8777 | 6.4694 | 76.9534 | 108.6446 | 64.7149 | 879.6099 | 884.6976 | 946.1147 | 2710.4231 | 2926.9327 |  | 2787.3765 | -0.047678 | -2.9728 | -7.553 | 1.008 |  |  | 2.517 | 2.4447 | 2.5255 | 2.3867 | -3.2513 | -3.4552 | -4.0791 | -4.7386 | -5.594 | -6.7459 | 0.665 | -3.609 | -3.955 | -4.3726 | -5.0995 | -6.1552 | -7.0582 | 1.2738 | -3.5394 | -3.8827 | -4.5578 | -4.9898 | -5.9043 | -6.8062 | 1.0852
19 / 1200 | 13.1572 | 10.9876 | 14.952 | 3.4 | -8.6121 | -3.7839 | 70.5241 | 34.4026 | 65.349 | 11.2767 | 11.2066 | 2.6734 | 2.2333 | 673.5056 | 35.2847 | 607.7076 | 607.4952 | 179.2821 | 684.6212 | 0.56013 | 0.21353 | 0.31539 | 7.4121 | 0.98248 | 34.1384 | 1.1462 | 2.6441 | 314.2914 | 292.6511 | 0.068823 | 1.9128 | 573.2117 | 8.5182 | 0.64377 | 35.2847 | 35.0464 | -8.482 | -12.3021 | -0.00025425 | 20.2979 | 3.69 | -8.7769 | -2.8311 | 77.6469 | 31.986 | 74.893 | 11.5746 | 11.386 | 2.7129 | 2.2056 | 693.2101 | 36.3011 | 608.6154 | 558.3292 | 180.1104 | 699.1538 | 0.64722 | 0.23776 | 0.35271 | 7.2847 | 0.97661 | 34.0704 | 2.2307 | 2.7356 | 313.367 | 295.499 | 0.064689 | 1.8899 | 574.9884 | 9.7369 | 3.6765 | 36.3011 | 35.6624 | -8.1389 | -12.5679 | 0.44544 | 20.5637 | 3.791 | 558.3292 | -3.7289 | 71.5708 | 34.0833 | 72.6255 | 11.22 | 11.0208 | 2.6985 | 2.2188 | 689.2994 | 35.0919 | 607.5356 | 558.477 | 0.57659 | 687.0353 | 0.57659 | 0.22666 | 0.42195 | 7.378 | 0.98155 | 33.7576 | 1.3342 | 2.5583 | 339.5327 | 292.1105 | 0.15049 | 1.7173 | 573.3901 | 8.7075 | 0.32027 | 35.0919 | 34.4036 | -8.2561 | -12.4364 | -0.48035 | 20.4322 | 3.4777 | 30.0419 | 35.0466 | 35.217 | 34.884 | 469.9334 | -0.69426 | -2.193 | 1.7882 | 7.7398 | 7.4835 | 8.764 | 24.9016 | 0.59914 | 978.2452 | 0.70946 | 5.0528 | 0.019951 | 2.3315 | 4.9669 | 6.0406 | 2.5306 | 8.4823 | 2.4845 | 4.0984 | 7.3697 | 10.3327 | 2.0681 | 9.7917 | 2.6685 | 4.2185 | 8.5758 | 11.1919 | 3.4951 | 9.1975 | 4.3295 | 6.0147 | 9.1012 | 10.6944 | 5.6569 | 5.0098 | 0.019951 | 11.1919 | 8.434 | 9.6765 | 6.9758 | -0.36636 | 7.9958 | 8.3621 | 5.52 | 77.1076 | 47.9576 | 64.7612 | 867.8575 | 870.5099 | 935.9122 | 2674.2791 | 2830.2203 |  | 2751.3867 | -0.027833 | -8.2923 | -12.3999 | -3.448 |  |  | 2.0238 | 1.9734 | 2.027 | 2.0599 | -8.6121 | -8.7993 | -9.3298 | -9.9332 | -10.6153 | -11.6634 | -3.7839 | -8.7769 | -9.122 | -9.5599 | -10.2345 | -11.1444 | -11.9627 | -2.8311 | -8.9587 | -9.2137 | -9.8544 | -10.2101 | -10.9719 | -11.794 | -3.7289
19 / 1800 | 12.7706 | 14.3663 | 13.8581 | 3.4 | -2.3079 | 1.46 | 65.1604 | 35.1273 | 61.048 | 11.4008 | 11.1209 | 3.4597 | 2.8791 | 663.8828 | 35.7148 | 608.0951 | 607.234 | 194.7358 | 672.7484 | 0.59628 | 0.19293 | 0.32497 | 9.2276 | 0.98465 | 34.3133 | 1.4015 | 3.0909 | 328.7728 | 293.8519 | 0.11115 | 2.3094 | 579.161 | 8.0195 | -0.37328 | 35.7148 | 34.754 | -2.1303 | -6.5594 | -0.41107 | 14.883 | 4.2516 | -2.6537 | 1.7281 | 69.438 | 34.87 | 67.477 | 11.652 | 11.3438 | 3.4778 | 2.8204 | 676.9896 | 36.5638 | 608.8496 | 564.4962 | 195.0524 | 681.2256 | 0.65203 | 0.2025 | 0.33724 | 9.019 | 0.98099 | 34.3624 | 2.2014 | 3.2203 | 319.6254 | 296.2357 | 0.074854 | 2.3455 | 579.9112 | 8.7648 | 0.65074 | 36.5638 | 35.5207 | -2.0021 | -7.0367 | 0.14238 | 15.3603 | 4.383 | 564.4962 | 1.919 | 65.4171 | 34.4582 | 66.6855 | 11.3027 | 10.8807 | 3.4896 | 2.869 | 676.3248 | 35.3797 | 607.7958 | 564.9342 | 0.60499 | 673.5984 | 0.60499 | 0.20669 | 0.44004 | 9.1966 | 0.98196 | 33.8505 | 1.5292 | 2.9272 | 357.9309 | 292.9132 | 0.2065 | 2.0418 | 580.0211 | 8.5594 | -0.5422 | 35.3797 | 33.916 | -1.913 | -6.6405 | -0.97803 | 14.9641 | 4.0668 | 30.0476 | 35.1651 | 35.3784 | 34.8941 | 534.4485 | 1.8359 | 2.0963 | 2.7994 | 7.6382 | 8.1446 | 9.188 | 25.9838 | 0.51591 | 975.0511 | 2.8628 | 5.6368 | 3.1915 | 3.8451 | 5.2237 | 5.5961 | 3.3341 | 7.0572 | 3.9644 | 4.731 | 6.2346 | 8.0357 | 3.8702 | 8.6504 | 4.5178 | 5.5047 | 7.3269 | 9.6831 | 5.5561 | 9.364 | 6.2294 | 7.5262 | 8.9208 | 10.5802 | 6.1435 | 5.6164 | 2.8628 | 10.5802 | 5.8023 | 6.0483 | 6.3885 | 2.2439 | 8.3236 | 6.0797 | 6.6968 | 77.0206 | 154.5175 | 64.7041 | 887.8211 | 878.2739 | 954.4057 | 2720.5015 | 2982.9874 |  | 2797.5221 | -0.062175 | -2.0151 | -6.7389 | 1.7024 |  |  | 2.6079 | 2.5244 | 2.6199 | 2.4615 | -2.3079 | -2.5248 | -3.1676 | -3.8567 | -4.7495 | -5.9486 | 1.46 | -2.6537 | -3.007 | -3.4583 | -4.1991 | -5.3338 | -6.2912 | 1.7281 | -2.5736 | -2.9218 | -3.6304 | -4.0707 | -5.0319 | -5.9535 | 1.919
24 | 12.433 | 12.9577 | 13.7843 | 4.186 | -4.4779 | -0.61089 | 66.1074 | 34.508 | 61.7378 | 11.2308 | 11.016 | 3.1631 | 2.6251 | 665.9068 | 35.1325 | 607.574 | 606.905 | 189.2727 | 675.2949 | 0.57658 | 0.18884 | 0.28276 | 8.529 | 0.98454 | 34.2236 | 0.90891 | 3.0554 | 307.3493 | 292.2217 | 0.047994 | 2.2965 | 576.7474 | 8.0614 | -0.11849 | 35.1325 | 34.3895 | -4.3565 | -8.6723 | -0.64735 | 17.6103 | 4.1943 | -4.8463 | -0.025996 | 71.5106 | 33.3537 | 69.3133 | 11.4695 | 11.2218 | 3.1763 | 2.5729 | 681.4833 | 35.948 | 608.3029 | 562.1858 | 189.5113 | 686.2146 | 0.64713 | 0.20451 | 0.29848 | 8.3327 | 0.9795 | 34.2248 | 1.7232 | 3.1673 | 300.7255 | 294.506 | 0.023528 | 2.3075 | 578.0145 | 9.095 | 1.7486 | 35.948 | 35.1023 | -4.2596 | -9.121 | -0.11722 | 18.059 | 4.2747 | 562.1858 | 0.0019776 | 66.748 | 34.0246 | 67.9601 | 11.1583 | 10.834 | 3.1851 | 2.6187 | 679.4834 | 34.8832 | 607.3501 | 562.6207 | 0.59015 | 676.8849 | 0.59015 | 0.20526 | 0.40507 | 8.501 | 0.98124 | 33.7402 | 1.143 | 2.8762 | 340.7284 | 291.5245 | 0.15582 | 2.0138 | 577.85 | 8.7312 | -0.27282 | 34.8832 | 33.7517 | -4.1904 | -8.7293 | -0.99126 | 17.6673 | 3.9126 | 30.0338 | 35.0369 | 35.2195 | 34.743 | 438.7506 | -0.077998 | 0.2579 | 0.89899 | 7.8286 | 9.1862 | 9.7993 | 25.5707 | 0.60175 | 988.5725 | 1.5566 | 4.341 | 1.7155 | 2.7224 | 4.3297 | 4.8269 | 2.6819 | 7.4019 | 3.4188 | 4.3669 | 5.9346 | 8.432 | 3.1314 | 9.0537 | 4.0286 | 4.9034 | 7.5191 | 9.9218 | 4.6405 | 9.7447 | 6.5145 | 7.599 | 8.8295 | 10.3014 | 5.7465 | 4.8651 | 1.5566 | 10.3014 | 7.9066 | 8.9283 | 8.9003 | 0.35963 | 8.938 | 8.5784 | 6.6178 | 76.8944 | 75.3109 | 64.739 | 866.8549 | 861.437 | 950.5322 | 2678.8254 | 2860.9331 |  | 2755.7198 | -0.036773 | -4.2688 | -8.8277 | -0.21164 |  |  | 2.3969 | 2.3202 | 2.4033 | 2.4698 | -4.4779 | -4.6878 | -5.2662 | -5.9318 | -6.7389 | -7.8897 | -0.61089 | -4.8463 | -5.2097 | -5.6533 | -6.3641 | -7.459 | -8.3076 | -0.025996 | -4.8167 | -5.1502 | -5.8017 | -6.2035 | -7.101 | -7.982 | 0.0019776
26 | 12.1234 | #NUM! | 12.2855 | 4.186 | -1.6208 | 1.9439 | 89.2102 | 53.7155 | 82.613 | 18.0347 | 17.9342 | 3.5473 | 2.9358 | 692.139 | 54.8819 | 623.1194 | 622.9574 | 196.2652 | 707.7044 | 0.74622 | 0.25714 | 0.39127 | 8.8363 | 0.98443 | 53.6549 | 1.227 | 2.905 | 363.2246 | 350.1543 | 0.047882 | 1.9134 | 579.7529 | 8.0589 | 0.91619 | 54.8819 | 54.6317 | -1.5116 | -6.1151 | -0.022536 | 15.3892 | 4.4943 | -2.0601 | 2.5306 | 96.5375 | 51.0435 | 93.2099 | 18.4067 | 18.1723 | 3.5481 | 2.8812 | 716.098 | 55.7997 | 623.7041 | 565.0294 | 196.2763 | 723.9143 | 0.86326 | 0.28621 | 0.46038 | 8.6316 | 0.97938 | 53.5342 | 2.2655 | 3.0183 | 366.0379 | 353.0055 | 0.048557 | 1.8546 | 581.0467 | 9.0838 | 4.1795 | 55.7997 | 55.2229 | -1.5072 | -6.5531 | 0.38215 | 15.8273 | 4.4931 | 565.0294 | 2.2467 | 91.278 | 51.837 | 93.2864 | 17.9241 | 17.6707 | 3.5676 | 2.9373 | 717.552 | 54.6065 | 622.941 | 565.5257 | 0.79441 | 712.8548 | 0.79441 | 0.27663 | 0.5311 | 8.8498 | 0.98297 | 53.2325 | 1.374 | 2.8749 | 392.5581 | 349.3021 | 0.15807 | 1.6618 | 580.2833 | 8.35 | 2.134 | 54.6065 | 53.971 | -1.3656 | -6.1033 | -0.63386 | 15.3775 | 4.1686 | 49.8873 | 54.6542 | 54.8408 | 54.6048 | 436.7203 | 1.319 | 1.8473 | 2.6952 | 8.4989 | 9.2209 | 10.1027 | 24.569 | 0.57338 | 984.99 | 3.0461 | 5.5575 | 3.1441 | 4.2846 | 5.3279 | 6.0184 | 3.9271 | 7.7908 | 4.4667 | 5.6117 | 7.155 | 9.204 | 4.2985 | 9.3041 | 5.0153 | 6.1693 | 8.2669 | 10.5557 | 5.6135 | 9.987 | 7.2489 | 8.7145 | 9.4538 | 10.8529 | 6.7089 | 6.0939 | 3.0443 | 10.8529 | 7.18 | 7.3736 | 7.4076 | 1.9538 | 9.2742 | 7.3204 | 5.4298 | 76.9955 | 74.3593 | 64.7922 | 1205.0817 | 1220.5263 | 1327.9369 | 3753.5381 | 3941.2768 |  | 3830.5336 | -0.031444 | -1.4615 | -6.2518 | 2.2404 |  |  | 1.9866 | 1.9204 | 2.0078 | 1.4275 | -1.655 | -2.0878 | -2.7347 | -3.5123 | -4.3678 | -5.5477 | 1.9262 | -2.0955 | -2.6589 | -3.1717 | -3.9794 | -5.0568 | -5.9436 | 2.5032 | -1.9707 | -2.517 | -3.2473 | -3.7334 | -4.629 | -5.5384 | 2.2211
27 | 9.8011 | 10.799 | 11.8698 | 4.186 | -0.89615 | 2.8766 | 61.575 | 33.0607 | 57.5032 | 11.125 | 10.0167 | 3.7276 | 2.9847 | 657.1402 | 34.7683 | 607.2469 | 603.5988 | 199.4409 | 665.8932 | 0.56192 | 0.21056 | 0.44325 | 9.582 | 0.98177 | 33.8841 | 0.88421 | 2.6691 | 378.5679 | 291.2033 | 0.27641 | 1.9412 | 581.1687 | 8.5891 | -2.2691 | 34.7683 | 30.7916 | -0.2254 | -5.7124 | -3.9365 | 14.7447 | 4.8163 | -0.58573 | 2.5075 | 61.1011 | 33.4429 | 59.5052 | 11.284 | 10.1798 | 3.7565 | 2.9738 | 660.9324 | 35.3161 | 607.739 | 565.8624 | 199.9346 | 664.3714 | 0.54086 | 0.20392 | 0.50084 | 9.551 | 0.98318 | 33.8019 | 1.5142 | 2.6522 | 383.1997 | 292.7348 | 0.28717 | 1.8848 | 580.5663 | 8.3066 | -2.0469 | 35.3161 | 31.3961 | -0.026349 | -5.7992 | -3.3027 | 14.8314 | 5.2134 | 565.8624 | 2.0389 | 61.2432 | 34.018 | 61.5105 | 11.2834 | 10.6251 | 3.5416 | 2.8943 | 665.2543 | 35.3143 | 607.7374 | 565.1637 | 0.52902 | 664.6788 | 0.52902 | 0.18307 | 0.42823 | 9.2899 | 0.98239 | 34.174 | 1.1403 | 2.8896 | 354.1998 | 292.7296 | 0.19514 | 2.0987 | 580.1121 | 8.4717 | -1.007 | 35.3143 | 33.011 | -1.536 | -6.4329 | -2.1065 | 15.4651 | 4.5872 | 30.0162 | 34.7281 | 34.6988 | 35.1174 | 406.0419 | 1.5998 | 2.2799 | 2.9439 | 7.8934 | 8.9975 | 10.206 | 24.3319 | 0.58718 | 974.6441 | 2.9655 | 5.6893 | 3.3778 | 4.3923 | 5.2854 | 6.0417 | 3.6447 | 7.865 | 4.5595 | 5.3235 | 6.5359 | 8.4699 | 4.048 | 9.2781 | 5.0727 | 7.1243 | 7.5965 | 10.5625 | 5.5033 | 9.8693 | 6.8045 | 7.647 | 8.8995 | 10.8977 | 6.5606 | 6.2888 | 2.9655 | 10.8977 | 6.2936 | 6.7176 | 7.2621 | 2.2746 | 9.0323 | 6.7577 | 5.9246 | 76.9054 | 74.9687 | 64.8129 | 885.4687 | 800.8515 | 761.3304 | 2447.6526 | 2622.0275 |  | 2524.5579 | -0.037171 | -0.59592 | -5.98 | 2.4743 |  |  | 2.8232 | 2.7972 | 2.6725 | 2.4204 | -0.89615 | -1.4153 | -2.1926 | -3.0519 | -4.0333 | -5.2692 | 2.8766 | -0.58573 | -1.3577 | -2.0135 | -2.899 | -4.1561 | -5.1711 | 2.5075 | -1.8457 | -2.3652 | -3.1415 | -3.685 | -4.7363 | -5.804 | 2.0389
28 | 10.507 | 11.818 | 12.1939 | 4.186 | 1.9014 | 4.7001 | 85.9959 | 52.9493 | 79.4006 | 17.8587 | 17.2299 | 4.1394 | 3.3567 | 685.0565 | 54.4432 | 622.8346 | 621.7707 | 206.322 | 700.6497 | 0.78269 | 0.31435 | 0.55636 | 10.0593 | 0.98666 | 53.2069 | 1.2363 | 2.4905 | 437.4597 | 348.7977 | 0.32354 | 1.4609 | 582.6854 | 7.5799 | -0.099459 | 54.4432 | 52.8499 | 2.5403 | -2.8798 | -1.4834 | 12.5129 | 4.7812 | 2.1743 | 4.823 | 85.6442 | 53.1413 | 83.1357 | 18.0297 | 17.2599 | 4.1702 | 3.3603 | 693.3971 | 54.8697 | 623.1117 | 569.0926 | 206.8158 | 699.3277 | 0.76652 | 0.32347 | 0.69254 | 10.0625 | 0.98616 | 52.8445 | 2.0252 | 2.3701 | 457.6969 | 350.1164 | 0.39407 | 1.2587 | 582.89 | 7.6786 | -0.21477 | 54.8697 | 52.9265 | 2.7375 | -2.8555 | -1.1901 | 12.4887 | 5.0299 | 569.0926 | 4.688 | 85.5678 | 53.076 | 85.7426 | 18.1056 | 17.6727 | 3.9833 | 3.2929 | 699.3401 | 55.0582 | 623.2331 | 568.546 | 0.74365 | 698.9269 | 0.74365 | 0.25812 | 0.55458 | 9.8289 | 0.98435 | 53.6907 | 1.3675 | 2.8812 | 406.046 | 350.7004 | 0.20308 | 1.7379 | 582.9616 | 8.0432 | 0.89988 | 55.0582 | 53.9759 | 1.5073 | -3.3552 | -1.0605 | 12.9883 | 4.4881 | 49.851 | 54.3333 | 54.1167 | 55.0364 | 398.2286 | 3.2301 | 3.8652 | 4.6734 | 8.6177 | 9.6333 | 10.6486 | 23.7119 | 0.54664 | 970.5537 | 5.3332 | 7.7408 | 5.7775 | 6.5609 | 7.3693 | 8.0721 | 5.6592 | 9.4384 | 6.6029 | 7.1191 | 8.1788 | 9.5154 | 6.0272 | 10.6417 | 6.9677 | 8.3896 | 9.0573 | 11.4376 | 7.2345 | 11.1821 | 8.5059 | 9.2462 | 10.2233 | 11.9313 | 8.2588 | 8.1254 | 5.3332 | 11.9313 | 5.3876 | 5.7681 | 5.9752 | 3.9229 | 9.6332 | 5.7103 | 4.4576 | 77.1512 | 74.5772 | 64.7834 | 1300.6684 | 1207.9759 | 1110.5316 | 3619.1782 | 3800.8651 |  | 3696.3294 | -0.027503 | 2.2617 | -3.0286 | 4.7371 |  |  | 2.3549 | 2.3533 | 2.2615 | 1.2316 | 1.9014 | 1.2381 | 0.46123 | -0.42979 | -1.3663 | -2.5275 | 4.7001 | 2.1743 | 1.2897 | 0.68771 | -0.25047 | -1.4024 | -2.3983 | 4.823 | 1.1329 | 0.45924 | -0.34329 | -0.92815 | -1.9618 | -2.95 | 4.688
34 | 10.2683 | 12.4014 | 11.8122 | 4.186 | -1.974 | 1.2847 | 67.9132 | 38.2486 | 62.9373 | 12.5157 | 11.6935 | 3.5542 | 2.8377 | 664.4123 | 39.3931 | 611.315 | 608.9722 | 196.3872 | 675.3413 | 0.5794 | 0.23206 | 0.46574 | 9.0605 | 0.98381 | 38.6111 | 0.78198 | 2.4971 | 388.5128 | 304.2458 | 0.27443 | 1.7249 | 579.0562 | 8.1892 | -1.5458 | 39.3931 | 36.7027 | -1.4622 | -6.9046 | -2.7792 | 15.3202 | 4.9306 | -2.6771 | 0.64715 | 69.1326 | 39.2702 | 66.9729 | 12.8644 | 12.2985 | 3.4462 | 2.7471 | 672.1985 | 40.4975 | 612.2559 | 563.8167 | 194.4597 | 676.9611 | 0.56561 | 0.20888 | 0.45478 | 8.7581 | 0.98332 | 38.9143 | 1.5832 | 2.7078 | 362.3962 | 307.4005 | 0.18041 | 1.8876 | 578.366 | 8.2972 | -0.57666 | 40.4975 | 38.6935 | -2.2443 | -7.6501 | -1.1706 | 16.0657 | 4.973 | 563.8167 | 0.75317 | 68.0323 | 38.4834 | 67.8689 | 12.6582 | 12.1292 | 3.3572 | 2.7384 | 674.8094 | 39.8468 | 611.7031 | 563.7426 | 0.55409 | 675.1682 | 0.55409 | 0.20448 | 0.46268 | 8.7406 | 0.98246 | 38.8691 | 0.97769 | 2.7101 | 364.4481 | 305.5399 | 0.19242 | 1.8704 | 578.5939 | 8.4707 | -0.33924 | 39.8468 | 38.1442 | -2.8909 | -7.7175 | -1.7235 | 16.1331 | 4.6716 | 34.9562 | 39.482 | 39.8641 | 39.8677 | 395.4531 | 0.073821 | 1.0016 | 2.2446 | 6.4196 | 8.2841 | 10.543 | 24.0664 | 0.58571 | 987.3658 | 2.074 | 5.101 | 2.6019 | 4.1706 | 4.5632 | 5.7432 | 2.7451 | 7.2234 | 3.978 | 5.3374 | 5.9663 | 8.6449 | 2.8019 | 8.7076 | 4.36 | 7.1963 | 6.3786 | 10.4975 | 3.8435 | 9.1933 | 6.0009 | 7.5068 | 7.227 | 10.7027 | 5.9402 | 5.8471 | 2.074 | 10.7027 | 6.3458 | 7.2825 | 8.2985 | 1.1067 | 8.4156 | 7.3089 | 5.483 | 80.2864 | 75.1732 | 64.9267 | 971.7449 | 888.915 | 831.7502 | 2692.4065 | 2871.2752 |  | 2772.6929 | -0.034332 | -2.1991 | -7.4161 | 0.895 |  |  | 2.5067 | 2.3658 | 2.3745 | 2.0363 | -1.974 | -2.5763 | -3.2853 | -4.1406 | -5.0192 | -6.2824 | 1.2847 | -2.6771 | -3.3622 | -3.9013 | -4.7681 | -5.9082 | -6.9117 | 0.64715 | -3.0459 | -3.651 | -4.4044 | -4.9729 | -5.9548 | -7.0265 | 0.75317
35 | 10.3771 | 12.4883 | 12.2033 | 4.186 | -3.4974 | -0.016044 | 62.7217 | 33.3274 | 58.2555 | 11.0407 | 10.1975 | 3.3483 | 2.6672 | 659.0343 | 34.4756 | 606.9829 | 604.2237 | 192.704 | 668.6138 | 0.53585 | 0.21155 | 0.42524 | 8.6993 | 0.98336 | 33.7456 | 0.72997 | 2.5337 | 367.6972 | 290.3866 | 0.24419 | 1.8263 | 577.5885 | 8.2952 | -1.8653 | 34.4756 | 31.4622 | -2.9571 | -8.3112 | -3.0988 | 16.0507 | 4.8139 | -4.1767 | -0.77723 | 64.001 | 34.4094 | 62.035 | 11.3484 | 10.8002 | 3.2489 | 2.5804 | 666.1778 | 35.5368 | 607.9365 | 562.2619 | 190.8678 | 670.4123 | 0.52472 | 0.19009 | 0.39495 | 8.4133 | 0.98349 | 34.089 | 1.4477 | 2.7606 | 337.5167 | 293.3526 | 0.1404 | 2.0094 | 576.6759 | 8.2756 | -0.77747 | 35.5368 | 33.6319 | -3.7057 | -9.0528 | -1.3385 | 16.7922 | 4.8761 | 562.2619 | -0.41887 | 63.2385 | 33.8158 | 63.1059 | 11.161 | 10.6501 | 3.1525 | 2.5728 | 669.0659 | 34.893 | 607.3592 | 562.1942 | 0.51964 | 669.3504 | 0.51964 | 0.19202 | 0.42121 | 8.3883 | 0.98144 | 33.9399 | 0.95311 | 2.7063 | 346.2373 | 291.5517 | 0.17317 | 1.9382 | 577.3386 | 8.6953 | -0.71581 | 34.893 | 33.1 | -4.4307 | -9.1141 | -1.7718 | 16.8536 | 4.492 | 29.9968 | 34.561 | 34.9705 | 34.8718 | 397.7991 | -1.0145 | -0.080025 | 1.2219 | 5.9091 | 7.602 | 9.7073 | 24.2203 | 0.59084 | 987.2409 | 0.97833 | 4.583 | 1.3422 | 3.4893 | 4.0819 | 5.6236 | 1.9265 | 7.0918 | 2.9924 | 4.6553 | 5.7694 | 8.7447 | 1.7506 | 8.4972 | 3.2761 | 6.518 | 6.158 | 10.5524 | 3.0308 | 8.6862 | 5.1038 | 6.6812 | 6.9551 | 10.2592 | 5.3645 | 5.3637 | 0.97833 | 10.5524 | 6.9236 | 7.682 | 8.4854 | 0.042473 | 7.7395 | 7.697 | 5.7739 | 80.2874 | 75.018 | 64.8956 | 877.7726 | 808.9881 | 756.1159 | 2442.8722 | 2620.6593 |  | 2523.1596 | -0.037201 | -3.6978 | -8.8138 | -0.40405 |  |  | 2.5197 | 2.3785 | 2.3837 | 2.3633 | -3.4974 | -4.0206 | -4.7117 | -5.5319 | -6.3911 | -7.6377 | -0.016044 | -4.1767 | -4.7932 | -5.3072 | -6.1687 | -7.2895 | -8.284 | -0.77723 | -4.6221 | -5.1505 | -5.8779 | -6.4156 | -7.3712 | -8.4056 | -0.41887
29no_ceil | 10.1278 | 10.9327 | 11.9147 | 4.186 | 0.8468 | 4.2272 | 73.1499 | 43.1374 | 67.9423 | 14.242 | 13.3935 | 3.987 | 3.2091 | 669.992 | 44.6712 | 615.6914 | 613.6256 | 203.8147 | 681.7366 | 0.65674 | 0.25178 | 0.49737 | 9.9473 | 0.98355 | 43.6071 | 1.0641 | 2.6087 | 407.6261 | 319.4722 | 0.29759 | 1.739 | 582.5256 | 8.2096 | -1.0034 | 44.6712 | 42.134 | 1.5349 | -3.9824 | -2.4263 | 13.4716 | 4.8292 | 1.3253 | 4.1564 | 72.0781 | 43.2427 | 70.1503 | 14.3737 | 13.389 | 4.0447 | 3.2276 | 674.5664 | 45.0557 | 615.9976 | 568.0106 | 204.7672 | 678.9212 | 0.62936 | 0.25412 | 0.61147 | 10.0075 | 0.98459 | 43.2939 | 1.7618 | 2.4771 | 426.8637 | 320.5967 | 0.35973 | 1.5543 | 582.3131 | 8.0004 | -1.1227 | 45.0557 | 42.1201 | 1.9169 | -3.844 | -2.2079 | 13.3332 | 5.1693 | 568.0106 | 3.9758 | 72.8615 | 43.6016 | 72.9793 | 14.4366 | 13.8916 | 3.8272 | 3.151 | 680.7624 | 45.2382 | 616.1424 | 567.3732 | 0.62655 | 680.4966 | 0.62655 | 0.21527 | 0.49322 | 9.7383 | 0.98262 | 43.9828 | 1.2554 | 2.9107 | 381.7641 | 321.1314 | 0.20553 | 1.9526 | 582.3484 | 8.4009 | 0.035043 | 45.2382 | 43.6366 | 0.45658 | -4.4251 | -1.4569 | 13.9143 | 4.4856 | 39.9552 | 44.5603 | 44.328 | 45.0935 | 405.9775 | 2.7792 | 3.3724 | 4.028 | 8.6067 | 9.4084 | 10.4525 | 24.1218 | 0.56936 | 971.0176 | 4.7378 | 7.1661 | 5.1049 | 5.9044 | 6.842 | 7.4465 | 5.1503 | 9.0173 | 6.0741 | 6.4966 | 7.7348 | 9.108 | 5.5646 | 10.3514 | 6.5143 | 7.9475 | 8.747 | 11.1412 | 6.8431 | 10.901 | 8.1228 | 8.7803 | 9.9562 | 11.609 | 7.8026 | 7.5907 | 4.7378 | 11.609 | 5.8275 | 6.036 | 6.4245 | 3.3932 | 9.4892 | 6.096 | 5.2459 | 76.9373 | 74.7664 | 64.777 | 1077.5247 | 988.1705 | 917.546 | 2983.2409 | 3159.9129 |  | 3060.1782 | -0.031562 | 1.3028 | -4.085 | 4.1198 | -0.046033 | -0.34369 | 2.6334 | 2.6514 | 2.5306 | 1.7584 | 0.8468 | 0.24662 | -0.53974 | -1.4405 | -2.4179 | -3.6214 | 4.2272 | 1.3253 | 0.47029 | -0.19819 | -1.1085 | -2.3311 | -3.3504 | 4.1564 | 0.060545 | -0.54801 | -1.3469 | -1.9202 | -2.9682 | -4.0382 | 3.9758
29ceil | 10.6006 | 11.6491 | 11.9111 | 4.186 | -0.80595 | 3.0093 | 74.2419 | 43.3118 | 68.774 | 14.2301 | 13.5592 | 3.7457 | 3.0156 | 671.9117 | 44.6363 | 615.6634 | 614.0419 | 199.7522 | 684.2269 | 0.64381 | 0.25114 | 0.48057 | 9.3903 | 0.9823 | 43.5738 | 1.0625 | 2.5641 | 398.8438 | 319.3702 | 0.26821 | 1.713 | 581.2592 | 8.479 | -0.67371 | 44.6363 | 42.6381 | -0.099804 | -5.4697 | -1.8829 | 14.2692 | 4.6638 | -0.56561 | 2.5354 | 73.7674 | 43.5342 | 71.5326 | 14.4109 | 13.6787 | 3.7636 | 3.0037 | 677.5749 | 45.1637 | 616.0833 | 566.12 | 200.0534 | 682.6176 | 0.62282 | 0.24676 | 0.56774 | 9.363 | 0.98418 | 43.4173 | 1.7464 | 2.5243 | 407.8781 | 320.913 | 0.29463 | 1.6154 | 580.4748 | 8.1005 | -0.53508 | 45.1637 | 42.9991 | 0.021412 | -5.5651 | -1.4505 | 14.3646 | 4.9995 | 566.12 | 2.2358 | 74.1379 | 43.3097 | 74.0048 | 14.4218 | 13.9949 | 3.5579 | 2.9255 | 683.12 | 45.1953 | 616.1083 | 565.4389 | 0.61315 | 683.42 | 0.61315 | 0.21391 | 0.46599 | 9.1096 | 0.98263 | 43.9685 | 1.2268 | 2.8666 | 368.4138 | 321.0055 | 0.16065 | 1.9302 | 580.3128 | 8.4192 | 0.634 | 45.1953 | 43.9437 | -1.4201 | -6.1834 | -1.1194 | 14.9828 | 4.4121 | 39.9229 | 44.521 | 44.4496 | 45.0631 | 399.6894 | 1.0984 | 2.0761 | 3.1357 | 6.8231 | 8.6931 | 10.882 | 24.1561 | 0.59627 | 970.6807 | 2.8791 | 5.8606 | 3.4513 | 4.8121 | 5.2201 | 6.3387 | 3.4536 | 7.5959 | 4.5984 | 5.8118 | 6.5248 | 8.8782 | 3.6042 | 9.0429 | 4.9949 | 7.6043 | 6.9555 | 10.8029 | 4.5687 | 9.6286 | 6.582 | 8.0212 | 7.8476 | 11.1256 | 6.5085 | 6.4299 | 2.8791 | 11.1256 | 5.7247 | 6.6171 | 7.7463 | 2.1034 | 8.7994 | 6.696 | 5.2585 | 77.2421 | 74.9905 | 64.9046 | 1077.2887 | 975.4505 | 922.2171 | 2974.9496 | 3151.3311 |  | 3052.1917 | -0.031459 | -0.49949 | -5.7392 | 2.5935 | -0.077321 | -0.34282 | 2.4559 | 2.4381 | 2.3405 | 1.7675 | -0.80595 | -1.3989 | -2.1203 | -3.0005 | -3.907 | -5.1223 | 3.0093 | -0.56561 | -1.3813 | -1.9923 | -2.8811 | -4.0409 | -5.0597 | 2.5354 | -1.7713 | -2.3459 | -3.1014 | -3.6724 | -4.6522 | -5.7066 | 2.2358
30 | 10.5054 | 11.802 | 11.9673 | 4.186 | -1.0217 | 2.4359 | 74.0623 | 43.2561 | 68.589 | 14.2103 | 13.5223 | 3.7155 | 2.9885 | 671.5567 | 44.5783 | 615.617 | 613.9506 | 199.2263 | 683.8821 | 0.63705 | 0.25295 | 0.48806 | 9.3328 | 0.98408 | 43.5225 | 1.0558 | 2.5192 | 401.6406 | 319.2007 | 0.27812 | 1.6684 | 580.3722 | 8.1217 | -0.72931 | 44.5783 | 42.5268 | -0.31241 | -5.6858 | -1.937 | 14.4908 | 4.6641 | -1.0263 | 2.1286 | 74.1701 | 43.5817 | 71.8922 | 14.4159 | 13.7294 | 3.6991 | 2.9516 | 678.3714 | 45.1783 | 616.0949 | 565.6603 | 198.9317 | 683.5096 | 0.62071 | 0.24658 | 0.56171 | 9.2151 | 0.98415 | 43.427 | 1.7513 | 2.5174 | 404.9068 | 320.9557 | 0.28444 | 1.6117 | 580.0022 | 8.1106 | -0.43053 | 45.1783 | 43.1512 | -0.43202 | -5.9819 | -1.3098 | 14.7869 | 4.9556 | 565.6603 | 1.7736 | 74.4116 | 43.2933 | 74.2604 | 14.4171 | 14.0106 | 3.5048 | 2.88 | 683.7093 | 45.1817 | 616.0976 | 565.0312 | 0.61035 | 684.0499 | 0.61035 | 0.21472 | 0.4647 | 8.9867 | 0.98311 | 43.9525 | 1.2292 | 2.8429 | 367.2353 | 320.9657 | 0.15678 | 1.9089 | 579.7129 | 8.326 | 0.69688 | 45.1817 | 43.9902 | -1.8047 | -6.5525 | -1.0574 | 15.3575 | 4.3626 | 39.9213 | 44.4638 | 44.461 | 45.0476 | 397.4445 | 0.88453 | 1.8415 | 3.0192 | 6.8563 | 8.6761 | 10.8826 | 24.1531 | 0.59176 | 968.257 | 2.5886 | 5.6491 | 3.1926 | 4.6211 | 5.0285 | 6.1883 | 3.1631 | 7.4117 | 4.3137 | 5.6538 | 6.3032 | 8.7689 | 3.2739 | 8.8405 | 4.7262 | 7.5021 | 6.7198 | 10.6958 | 4.2911 | 9.4629 | 6.3551 | 7.8411 | 7.6316 | 11.0053 | 6.3012 | 6.243 | 2.5886 | 11.0053 | 5.9718 | 6.8346 | 7.8634 | 1.9151 | 8.805 | 6.8899 | 5.189 | 77.1225 | 74.1238 | 64.8952 | 1066.1441 | 987.3061 | 918.1036 | 2971.5634 | 3147.8758 |  | 3048.6859 | -0.031509 | -0.84972 | #REF! | 2.1127 | -0.07689 | -0.34236 | 2.4417 | 2.3915 | 2.3041 | 1.7462 | -1.0217 | -1.6279 | -2.339 | -3.217 | -4.1058 | -5.3291 | 2.4359 | -1.0263 | -1.827 | -2.4568 | -3.3161 | -4.4641 | -5.4723 | 2.1286 | -2.1899 | -2.755 | -3.5071 | -4.0665 | -5.035 | -6.0838 | 1.7736
31 | 10.5063 | 12.0078 | 12.0631 | 4.186 | -1.5224 | 1.7169 | 74.2372 | 43.2228 | 68.681 | 14.1836 | 13.513 | 3.6372 | 2.9173 | 671.848 | 44.4999 | 615.5542 | 613.927 | 197.8264 | 684.3524 | 0.62799 | 0.253 | 0.48579 | 9.1422 | 0.98479 | 43.4966 | 1.0033 | 2.483 | 399.9414 | 318.9719 | 0.27301 | 1.6401 | 579.448 | 7.9858 | -0.72435 | 44.4999 | 42.4984 | -0.88059 | -6.2689 | -1.9317 | 15.1413 | 4.7465 | -1.6907 | 1.4927 | 74.7817 | 43.6295 | 72.444 | 14.4077 | 13.7647 | 3.5997 | 2.8676 | 679.6403 | 45.1544 | 616.0759 | 564.8915 | 197.1498 | 684.9096 | 0.61591 | 0.24555 | 0.54967 | 8.9787 | 0.9839 | 43.4442 | 1.7102 | 2.5084 | 399.215 | 320.8856 | 0.26534 | 1.6104 | 579.2871 | 8.1693 | -0.37376 | 45.1544 | 43.2558 | -1.1556 | -6.6766 | -1.2219 | 15.5491 | 4.9859 | 564.8915 | 1.1315 | 74.853 | 43.2747 | 74.6784 | 14.3964 | 14.0117 | 3.4141 | 2.8009 | 684.7101 | 45.1217 | 616.0499 | 564.2997 | 0.60409 | 685.103 | 0.60409 | 0.21477 | 0.45736 | 8.7681 | 0.98306 | 43.9396 | 1.182 | 2.8139 | 363.2652 | 320.79 | 0.14387 | 1.8889 | 578.9667 | 8.3443 | 0.71887 | 45.1217 | 43.9935 | -2.4837 | -7.2129 | -1.0375 | 16.0853 | 4.4123 | 39.9195 | 44.4301 | 44.4777 | 45.0311 | 394.4677 | 0.66778 | 1.456 | 2.8403 | 7.0637 | 8.6404 | 10.9133 | 24.171 | 0.59289 | 978.9884 | 2.1872 | 5.3826 | 2.6594 | 4.4165 | 4.8388 | 6.1093 | 2.9109 | 7.4438 | 3.9453 | 5.5819 | 6.3511 | 9.0021 | 2.8668 | 8.831 | 4.3108 | 7.4403 | 6.7157 | 10.8196 | 3.9389 | 9.3219 | 5.9663 | 7.6291 | 7.5608 | 10.9702 | 6.1334 | 6.0378 | 2.1872 | 10.9702 | 6.3959 | 7.1843 | 8.073 | 1.6547 | 8.8725 | 7.2178 | 5.1394 | 77.0582 | 73.7518 | 64.9042 | 1056.9496 | 991.0174 | 917.0217 | 2964.9912 | 3141.1945 |  | 3042.0495 | -0.031559 | -1.5066 | #REF! | 1.447 | -0.080361 | -0.3455 | 2.3872 | 2.3215 | 2.2419 | 1.7332 | -1.5224 | -2.1256 | -2.8275 | -3.6816 | -4.5605 | -5.7857 | 1.7169 | -1.6907 | -2.47 | -3.0932 | -3.9468 | -5.0745 | -6.0823 | 1.4927 | -2.8006 | -3.3481 | -4.0975 | -4.6459 | -5.6155 | -6.6284 | 1.1315
32 | 10.109 | 10.8644 | 11.645 | 4.186 | 1.1893 | 4.3333 | 72.7587 | 43.2575 | 67.4919 | 14.2717 | 13.326 | 4.0261 | 3.2338 | 668.8765 | 44.7579 | 615.7602 | 613.4546 | 204.4705 | 680.7673 | 0.65167 | 0.25509 | 0.51234 | 10.0245 | 0.98396 | 43.7466 | 1.0113 | 2.5549 | 414.0103 | 319.7257 | 0.31848 | 1.6901 | 582.5986 | 8.1257 | -1.3296 | 44.7579 | 41.9279 | 1.7986 | -3.7924 | -2.8271 | 13.3819 | 4.9816 | 1.5174 | 4.0992 | 71.8342 | 43.3091 | 69.7388 | 14.4138 | 13.3766 | 4.0612 | 3.2337 | 673.5082 | 45.1719 | 616.0897 | 568.0652 | 205.0472 | 678.247 | 0.62336 | 0.2537 | 0.61542 | 10.0299 | 0.98512 | 43.477 | 1.6949 | 2.4574 | 428.453 | 320.9373 | 0.36428 | 1.5415 | 582.1807 | 7.8938 | -1.2257 | 45.1719 | 42.0833 | 2.0298 | -3.7945 | -2.4836 | 13.384 | 5.312 | 568.0652 | 3.7079 | 72.7069 | 43.4777 | 72.6462 | 14.4979 | 13.9338 | 3.8368 | 3.1526 | 679.8232 | 45.4154 | 616.2822 | 567.391 | 0.62092 | 679.9602 | 0.62092 | 0.21554 | 0.49998 | 9.7513 | 0.98404 | 44.1956 | 1.2198 | 2.8811 | 384.3367 | 321.6511 | 0.21277 | 1.9259 | 581.8607 | 8.1171 | 0.2846 | 45.4154 | 43.7623 | 0.52538 | -4.4092 | -1.6062 | 13.9987 | 4.6253 | 39.9166 | 44.7549 | 44.5669 | 45.3684 | 379.7138 | 2.5725 | 3.4383 | 4.3854 | 7.9084 | 9.6391 | 11.2209 | 24.292 | 0.59763 | 981.3327 | 4.1922 | 6.9376 | 4.7456 | 5.5681 | 6.5375 | 7.2696 | 4.7445 | 8.9843 | 5.7934 | 6.2823 | 7.7108 | 9.2879 | 5.119 | 10.4386 | 6.2713 | 8.0958 | 8.7473 | 11.5094 | 6.3805 | 11.051 | 7.9126 | 8.7518 | 9.9096 | 11.974 | 7.6756 | 7.4902 | 4.1922 | 11.974 | 5.3359 | 6.2008 | 6.8355 | 3.4654 | 9.5895 | 6.1241 | 5.1574 | 0 | 0 | 0 | 0 | 0 | 0 | 3000.1876 | 3176.1876 |  | 3000.1876 | -0.055413 | 1.4513 | -3.9987 | 4.0468 | -0.077416 | -0.38243 | 2.6616 | 2.6586 | 2.5304 | 1.7191 | 1.1893 | 0.55219 | -0.22909 | -1.1381 | -2.101 | -3.3231 | 4.3333 | 1.5174 | 0.64377 | 0.018149 | -0.94293 | -2.1618 | -3.1938 | 4.0992 | 0.21606 | -0.42314 | -1.2056 | -1.8021 | -2.8202 | -3.8965 | 3.7079
33 | 10.3715 | 11.2997 | 11.8193 | 4.186 | 0.026403 | 3.5405 | 73.6332 | 43.2671 | 68.2008 | 14.2306 | 13.458 | 3.856 | 3.0969 | 670.6142 | 44.6378 | 615.6646 | 613.7885 | 201.6286 | 682.8578 | 0.64674 | 0.25202 | 0.4909 | 9.6264 | 0.98276 | 43.606 | 1.0319 | 2.5666 | 403.9487 | 319.3747 | 0.28543 | 1.712 | 581.8222 | 8.3772 | -0.93619 | 44.6378 | 42.3309 | 0.65639 | -4.8367 | -2.2298 | 13.7776 | 4.8631 | 0.26986 | 3.1468 | 72.958 | 43.4156 | 70.7693 | 14.3921 | 13.5473 | 3.8757 | 3.09 | 675.9085 | 45.1092 | 616.04 | 566.8628 | 201.9612 | 680.85 | 0.62303 | 0.24934 | 0.58643 | 9.6141 | 0.98446 | 43.3996 | 1.7096 | 2.499 | 415.9491 | 320.7534 | 0.32238 | 1.5881 | 581.1539 | 8.0369 | -0.81313 | 45.1092 | 42.6025 | 0.7903 | -4.8902 | -1.8359 | 13.831 | 5.16 | 566.8628 | 2.9242 | 73.719 | 43.3501 | 73.5989 | 14.4354 | 13.9801 | 3.6567 | 3.0082 | 682.1639 | 45.2349 | 616.1397 | 566.1621 | 0.61898 | 682.4345 | 0.61898 | 0.21428 | 0.47434 | 9.337 | 0.98244 | 44.029 | 1.206 | 2.8889 | 372.748 | 321.1217 | 0.175 | 1.9457 | 581.1421 | 8.4513 | 0.54981 | 45.2349 | 43.8999 | -0.71967 | -5.5271 | -1.2417 | 14.468 | 4.5016 | 39.9277 | 44.5606 | 44.4384 | 45.1416 | 397.1773 | 1.618 | 2.5472 | 3.5124 | 7.0835 | 8.9827 | 10.7565 | 24.1391 | 0.57641 | 982.6943 | 3.9058 | 6.6767 | 4.5746 | 5.5336 | 6.0635 | 6.9832 | 4.3097 | 8.2611 | 5.5252 | 6.289 | 7.2348 | 9.0132 | 4.5651 | 9.7158 | 5.9329 | 7.9631 | 7.6799 | 11.0197 | 5.506 | 10.3142 | 7.4596 | 8.5561 | 8.5715 | 11.4439 | 7.2124 | 7.109 | 3.9058 | 11.4439 | 5.4655 | 6.4355 | 7.2441 | 2.5592 | 8.9409 | 6.3817 | 5.2457 | 77 | 0 | 0 | 0 | 0 | 0 | 2984.7877 | 3160.7877 |  | 3061.7877 | -0.031321 | 0.24234 | -5.0847 | 3.2038 | -0.076914 | -0.3477 | 2.5333 | 2.5219 | 2.4071 | 1.7575 | 0.026403 | -0.58599 | -1.3308 | -2.2095 | -3.1493 | -4.367 | 3.5405 | 0.26986 | -0.55279 | -1.1918 | -2.0965 | -3.2842 | -4.3089 | 3.1468 | -1.0255 | -1.6267 | -2.3807 | -2.9514 | -3.9588 | -4.9837 | 2.9242
40 | 9.5687 | 10.8386 | 10.6398 | 4.186 | 0.78774 | 4.5349 | 61.9582 | 32.8029 | 57.7246 | 11.107 | 9.6761 | 3.9527 | 3.1684 | 657.6753 | 34.7061 | 607.191 | 602.4053 | 203.2536 | 666.771 | 0.60206 | 0.22367 | 0.47107 | 10.105 | 0.98051 | 33.8653 | 0.84088 | 2.6919 | 391.2811 | 291.0297 | 0.31709 | 1.94 | 583.2626 | 8.8228 | -3.2865 | 34.7061 | 29.5164 | 1.31 | -4.2878 | -5.2495 | 14.4993 | 5.0756 | 1.051 | 3.4895 | 59.4938 | 33.5706 | 59.3696 | 11.351 | 10.1131 | 3.9868 | 3.1655 | 660.4215 | 35.5455 | 607.9443 | 567.4991 | 203.8202 | 660.6897 | 0.53315 | 0.19191 | 0.49969 | 10.1081 | 0.98562 | 33.9821 | 1.5634 | 2.7784 | 385.5463 | 293.377 | 0.293 | 1.9797 | 581.4108 | 7.8003 | -2.418 | 35.5455 | 31.1526 | 1.5376 | -4.3108 | -3.7661 | 14.5223 | 5.3618 | 567.4991 | 4.6012 | 59.3736 | 32.9237 | 61.0683 | 11.1075 | 9.8318 | 3.9057 | 3.1714 | 664.8592 | 34.708 | 607.1927 | 567.549 | 0.54565 | 661.2194 | 0.54565 | 0.2049 | 0.54427 | 10.0995 | 0.98029 | 33.6869 | 1.0212 | 2.6631 | 401.1686 | 291.035 | 0.34835 | 1.8401 | 583.3674 | 8.8665 | -2.8188 | 34.708 | 30.105 | 0.99351 | -4.2653 | -4.6102 | 14.4768 | 5.0303 | 30.0132 | 34.766 | 34.9187 | 34.7152 | 405.9145 | 3.0101 | 3.6378 | 4.2849 | 9.0723 | 9.9654 | 11.5967 | 24.9398 | 0.5845 | 980.4924 | 4.2567 | 6.83 | 4.7583 | 6.9596 | 6.4274 | 5.0769 | 4.8142 | 8.652 | 5.7498 | 9.229 | 7.5228 | 6.4924 | 5.1613 | 10.1213 | 6.2688 | 11.4576 | 8.5132 | 7.7935 | 6.5764 | 10.8011 | 8.0182 | 12.446 | 9.9445 | 9.9981 | 7.6612 | 7.2412 | 4.2567 | 12.446 | 6.0622 | 6.3276 | 7.3119 | 3.6443 | 10.2115 | 6.5672 | 5.7599 | 77.3109 | 76.1842 | 64.7683 | 928.1683 | 833.0099 | 777.3366 | 2538.3168 | 2701.2551 | 45.0209 | 2615.6277 | -0.031705 | 1.2804 | -4.2874 | 4.2086 | 0.015089 | -0.19257 | 3.029 | 2.9844 | 3.0114 | 2.2955 | 0.78774 | 0.21345 | -0.63066 | -1.5238 | -2.547 | -3.78 | 4.5349 | 1.051 | 0.28155 | -0.3728 | -1.2867 | -2.5298 | -3.5843 | 3.4895 | 0.765 | 0.021239 | -0.83687 | -1.4903 | -2.59 | -3.6533 | 4.6012
47 | 10.4819 | 12.6084 | 12.6394 | 4.186 | -2.4563 | 0.82376 | 63.4919 | 33.2525 | 59.1487 | 11.0302 | 10.0545 | 3.479 | 2.7793 | 660.9857 | 34.4393 | 606.9502 | 603.7339 | 195.0656 | 670.2953 | 0.57137 | 0.22093 | 0.43844 | 9.0249 | 0.98378 | 33.7938 | 0.64554 | 2.5873 | 374.2464 | 290.2853 | 0.26514 | 1.8441 | 578.5243 | 8.2008 | -2.3173 | 34.4393 | 30.9351 | -1.9973 | -7.377 | -3.7322 | 16.2384 | 4.9207 | -2.9852 | 0.24802 | 62.8386 | 34.3341 | 62.8479 | 11.3176 | 10.6371 | 3.399 | 2.703 | 668.0257 | 35.4313 | 607.8422 | 563.4121 | 193.6113 | 668.0055 | 0.52641 | 0.18992 | 0.42634 | 8.7668 | 0.9835 | 34.0558 | 1.3756 | 2.7718 | 351.232 | 293.0572 | 0.18481 | 1.9833 | 577.8781 | 8.2637 | -1.2822 | 35.4313 | 33.052 | -2.5888 | -8.0157 | -1.9479 | 16.8771 | 5.0305 | 563.4121 | 0.63284 | 62.2762 | 33.8867 | 64.4722 | 11.1326 | 10.484 | 3.294 | 2.6857 | 672.0844 | 34.7948 | 607.2708 | 563.261 | 0.52323 | 667.3732 | 0.52323 | 0.19499 | 0.46331 | 8.7107 | 0.98096 | 33.8293 | 0.96552 | 2.684 | 363.8589 | 291.2774 | 0.22969 | 1.871 | 578.6367 | 8.7855 | -1.3821 | 34.7948 | 32.5046 | -3.3557 | -8.1527 | -2.3361 | 17.0141 | 4.6785 | 30.0307 | 34.6674 | 34.9999 | 34.8407 | 399.8256 | 0.32492 | 0.84376 | 2.0575 | 7.6732 | 8.3623 | 10.5487 | 28.1697 | 0.58572 | 992.9878 | 1.5663 | 4.6727 | 1.8429 | 3.2569 | 4.2914 | 5.7825 | 2.8205 | 7.4243 | 3.3299 | 5.0131 | 6.2852 | 9.1384 | 2.8665 | 8.8388 | 3.7333 | 5.9246 | 7.6352 | 10.6223 | 4.355 | 9.0857 | 5.4717 | 8.2491 | 8.5581 | 11.0865 | 5.9105 | 5.6271 | 1.5663 | 11.0865 | 7.3483 | 7.5186 | 8.4912 | 1.0754 | 8.8614 | 7.786 | 5.6985 | 77.1868 | 75.5174 | 64.713 | 926.7452 | 841.1387 | 772.8834 | 2540.7687 | 2717.3452 | 45.2891 | 2617.9555 | -0.036574 | -2.6473 | -7.8417 | 0.56821 | 0.031059 | -0.14903 | 2.6387 | 2.5063 | 2.5014 | 2.2428 | -2.4563 | -2.959 | -3.6972 | -4.5298 | -5.424 | -6.6434 | 0.82376 | -2.9852 | -3.5916 | -4.2282 | -5.0404 | -6.2151 | -7.1547 | 0.24802 | -3.4741 | -3.9908 | -4.8066 | -5.3357 | -6.3422 | -7.3264 | 0.63284

## final overview
[5 empty] | 1 complete running cycle | [12 empty] | C1 | C2 | C3 | [5 empty] | 24h |  |  |  |  | C1 | C2 | C3 | C1 | C2 | C3 | C1 | C2 | C3
Test # | Spec | Condensing Temp | Gen | Ceiling | Product Temp [°C] |  |  |  | Temp class | COP compr | Qevap Qcond hevap in + Select massflow | Qevap,balance | DQevap % | Pcp,meas | Qevap,select0K | Pcp,sel | Qcond | xcd,out (mselect) | xcd,out (mselect) | xcd,out (mselect) | DPower % | DQevap % | Fans speed | Fans power | Aux power | TEC | EEI | Energy Label | Tair,in | Tair,out | C1: T disch; C1: T evap [°C]; C1: SH evap [K] | Tw,in [°C] | Tw,out [°C] | Tcond1 [°C] | Tcond2 [°C] | Tcond3 [°C] |  |  | Dhevap | Massflow select | Massflow select corrected | Massflow KlasBerglof
- |  | °C | - |  | AVG | MAX | MIN | MEDIAN |  | - | kW | [33 empty] | hsuc | hdis | kJ/kg
5 |  | 35 | 1 | no | 6.3618 | 10.2283 | 2.6833 | 5.8256 | 3H2 | 2.1473 | 5.7422 | 6.286 | 8.652% | 2.6737 | 7.4243 | 2.3645 | 8.826 | 15.3% | 7.62% | 18.58% | 13.08% | -22.66% | 1400 | 69.9419 | 77.6889 | 63.3463 | 49.77% | B | 10.4537 | 1.4547 | 72.1586 | 72.4441 | 69.7467 | -9.13 | -7.4241 | -8.3717 | 15.21 | 11.5699 | 13.5311 | 29.1568 | 34.3093 | 33.6102 | 34.832 | 33.9744 | 588700.0576 | 689490.5488 | 227.8543 | 26.2922 | 25.3741 | 25.201
4 |  | 55 |  | no | 6.1833 | 9.6647 | 2.7741 | 5.9679 | 3H2 | 1.2281 | 4.6481 | 4.5526 | -2.097% | 3.7848 | 6.9838 | 3.5173 | 8.1482 | 36.09% | 20.53% | 29.5% | 7.605% | -33.44% | 1400 | 69.3007 | 77.7157 | 82.6858 | 65% | C | 10.7072 | 4.2673 | 88.8698 | 91.0022 | 86.1075 | -3.7192 | -2.7251 | -2.9738 | 11.4638 | 7.6495 | 9.1624 | 48.7337 | 53.9158 | 52.7888 | 54.5707 | 53.3829 | 588662.2481 | 709184.5523 | 155.8032 | 30.1592 | 29.5833 | 29.833
18 | 1400rpm | 35 | 2 | no | 5.2427 | 10.7077 | 0.40121 | 4.6771 | 3H2 | 2.2376 | 6.031 | 5.9459 | -1.431% | 2.6935 | 6.7959 | 2.3988 | 8.5047 | 8.828% | 6.909% | 14.74% | 12.29% | -11.25% | 1400 | 73.0477 | 4.0725 | 62.4352 | 49.05% | B | 8.5133 | -0.60557 | 68.0399 | 74.1792 | 68.0242 | -9.8852 | -10.2807 | -10.2103 | 8.0539 | 9.3624 | 8.5806 | 30.0378 | 35.0876 | 34.9929 | 35.5153 | 34.3431 | 575303.0012 | 679564.0991 | 245.7366 | 24.4436 | 24.0625 | 24.5425
19 | 1600rpm | 35 |  | no | 5.6354 | 10.5038 | 1.7546 | 5.0459 | 3H2 | 2.3867 | 6.4694 | 6.44 | -0.4561% | 2.7104 | 7.6035 | 2.3942 | 9.0149 | 10.83% | 8.955% | 19.95% | 13.21% | -14.92% | 1400 | 108.6446 | -31.6912 | 63.5303 | 49.91% | B | 8.4083 | 1.5306 | 65.9647 | 71.1106 | 66.3658 | -7.3971 | -7.7908 | -7.4966 | 8.0621 | 9.0646 | 8.5818 | 30.0438 | 35.0745 | 34.7873 | 35.4528 | 33.9995 | 578253.0566 | 675290.559 | 243.804 | 27.0038 | 26.5902 | 26.5351
19 | 1200rpm | 35 |  | no | 5.6569 | 11.1919 | 0.019951 | 5.0098 | 3H2 | 2.0599 | 5.52 | 5.3975 | -2.27% | 2.6743 | 6.1271 | 2.3941 | 7.938 | 6.882% | 6.469% | 15.05% | 11.7% | -9.909% | 1400 | 47.9576 | 29.15 | 59.1942 | 46.51% | B | 7.9958 | -0.36636 | 70.5241 | 77.6469 | 71.5708 | -12.3021 | -12.5679 | -12.4364 | 8.5182 | 9.7369 | 8.7075 | 30.0419 | 35.0492 | 35.0464 | 35.6624 | 34.4036 | 573237.7795 | 684846.9032 | 242.4963 | 22.2748 | 21.9002 | 22.7631
19 | 1800rpm | 35 |  | no | 6.1435 | 10.5802 | 2.8628 | 5.6164 | 3H2 | 2.4615 | 6.6968 | 6.6539 | -0.6434% | 2.7205 | 7.8689 | 2.3941 | 9.2384 | 11.11% | 7.485% | 20.65% | 13.63% | -14.9% | 1400 | 154.5175 | -77.497 | 64.239 | 50.47% | C | 8.3236 | 2.2439 | 65.1604 | 69.438 | 65.4171 | -6.5594 | -7.0367 | -6.6405 | 8.0195 | 8.7648 | 8.5594 | 30.0476 | 35.1458 | 34.754 | 35.5207 | 33.916 | 579163.4623 | 673595.4976 | 244.687 | 27.8485 | 27.435 | 27.3686
24 |  | 35 |  | no | 5.7465 | 10.3014 | 1.5566 | 4.8651 | 3H2 | 2.4698 | 6.6178 | 6.554 | -0.9734% | 2.6788 | 7.2325 | 2.3766 | 9.0989 | 4.799% | 2.353% | 15.58% | 12.71% | -8.499% | 1400 | 75.3109 | 1.5834 | 61.3801 | 48.23% | B | 8.938 | 0.35963 | 66.1074 | 71.5106 | 66.748 | -8.6723 | -9.121 | -8.7293 | 8.0614 | 9.095 | 8.7312 | 30.0338 | 34.9998 | 34.3895 | 35.1023 | 33.7517 | 576748.6581 | 675936.4177 | 257.9314 | 25.7364 | 25.3373 | 25.6572
26 |  | 55 |  | no | 6.7089 | 10.8529 | 3.0443 | 6.0939 | 3H2 | 1.4275 | 5.4298 | 5.2323 | -3.774% | 3.7535 | 6.0052 | 3.5643 | 8.7982 | 4.788% | 4.856% | 15.81% | 5.309% | -9.582% | 1400 | 74.3593 | 2.6362 | 89.0405 | 69.96% | C | 9.2742 | 1.9538 | 89.2102 | 96.5375 | 91.278 | -6.1151 | -6.5531 | -6.1033 | 8.0589 | 9.0838 | 8.35 | 49.8873 | 54.6999 | 54.6317 | 55.2229 | 53.971 | 579755.499 | 707986.6283 | 195.2609 | 26.7029 | 26.3002 | 27.8081
27 |  | 35 | 3 | no | 6.5606 | 10.8977 | 2.9655 | 6.2888 | 3H2 | 2.4204 | 5.9246 | 5.8856 | -0.6631% | 2.4477 | 8.4184 | 2.2524 | 8.2109 | 27.64% | 28.72% | 19.51% | 8.67% | -29.62% | 1400 | 74.9687 | 1.9366 | 58.3901 | 45.88% | B | 9.0323 | 2.2746 | 61.575 | 61.1011 | 61.2432 | -5.7124 | -5.7992 | -6.4329 | 8.5891 | 8.3066 | 8.4717 | 30.0162 | 34.8481 | 30.7916 | 31.3961 | 33.011 | 581168.1221 | 669312.335 | 224.585 | 28.8526 | 28.4221 | 26.3803
28 |  | 55 |  | no | 8.2588 | 11.9313 | 5.3332 | 8.1254 | 3H2 | 1.2316 | 4.4576 | 4.3036 | -3.577% | 3.6192 | 7.0551 | 3.4944 | 7.7418 | 32.35% | 39.41% | 20.31% | 3.572% | -36.82% | 1400 | 74.5772 | 2.574 | 81.2271 | 63.82% | C | 9.6332 | 3.9229 | 85.9959 | 85.6442 | 85.5678 | -2.8798 | -2.8555 | -3.3552 | 7.5799 | 7.6786 | 8.0432 | 49.851 | 54.4955 | 52.8499 | 52.9265 | 53.9759 | 582684.8924 | 702436.5754 | 155.2547 | 30.3131 | 29.9453 | 28.7112
29no_ceil |  | 45 |  | no | 7.8026 | 11.609 | 4.7378 | 7.5907 | 3H2 | 1.7584 | 5.2459 | 5.1624 | -1.618% | 2.9832 | 7.9237 | 2.8136 | 7.9965 | 29.76% | 35.97% | 20.55% | 6.029% | -33.79% | 1400 | 74.7664 | 2.1709 | 69.5686 | 54.66% | C | 9.4892 | 3.3932 | 73.1499 | 72.0781 | 72.8615 | -3.9824 | -3.844 | -4.4251 | 8.2096 | 8.0004 | 8.4009 | 39.9552 | 44.6606 | 42.134 | 42.1201 | 43.6366 | 582525.8476 | 684263.3727 | 188.3175 | 30.1085 | 29.6885 | 27.8568
29ceil | demand | 45 |  | yes | 6.5085 | 11.1256 | 2.8791 | 6.4299 | 3H2 | 1.7675 | 5.2585 | 5.1288 | -2.528% | 2.9749 | 7.3397 | 2.8406 | 7.955 | 26.82% | 29.46% | 16.07% | 4.73% | -28.36% | 1400 | 74.9905 | 2.2515 | 69.6369 | 54.71% | C | 8.7994 | 2.1034 | 74.2419 | 73.7674 | 74.1379 | -5.4697 | -5.5651 | -6.1834 | 8.479 | 8.1005 | 8.4192 | 39.9229 | 44.6779 | 42.6381 | 42.9991 | 43.9437 | 581258.7752 | 686201.7863 | 195.2588 | 28.2687 | 27.8611 | 26.9308
30 | 4h | 45 |  | yes | 6.3012 | 11.0053 | 2.5886 | 6.243 | 3H2 | 1.7462 | 5.189 | 5.0566 | -2.62% | 2.9716 | 7.2345 | 2.841 | 7.8795 | 27.81% | 28.44% | 15.68% | 4.597% | -28.27% | 1400 | 74.1238 | 2.9987 | 69.098 | 54.29% | C | 8.805 | 1.9151 | 74.0623 | 74.1701 | 74.4116 | -5.6858 | -5.9819 | -6.5525 | 8.1217 | 8.1106 | 8.326 | 39.9213 | 44.6575 | 42.5268 | 43.1512 | 43.9902 | 580370.8717 | 685909.992 | 193.995 | 27.9132 | 27.5284 | 26.7482
31 | 5h | 45 |  | yes | 6.1334 | 10.9702 | 2.1872 | 6.0378 | 3H2 | 1.7332 | 5.1394 | 4.9886 | -3.024% | 2.965 | 7.0365 | 2.8397 | 7.8053 | 27.3% | 26.53% | 14.39% | 4.411% | -26.96% | 1400 | 73.7518 | 3.3065 | 70.09 | 55.07% | C | 8.8725 | 1.6547 | 74.2372 | 74.7817 | 74.853 | -6.2689 | -6.6766 | -7.2129 | 7.9858 | 8.1693 | 8.3443 | 39.9195 | 44.6463 | 42.4984 | 43.2558 | 43.9935 | 579445.5043 | 686325.4951 | 195.0125 | 27.2352 | 26.8628 | 26.3542
32 | 3h | 45 |  | yes | 7.6756 | 11.974 | 4.1922 | 7.4902 | 3H2 | 1.7191 | 5.1574 | 5.0432 | -2.264% | 3.0002 | 7.956 | 2.8116 | 7.8934 | 31.85% | 36.43% | 21.28% | 6.706% | -35.18% | 1400 | 0 | 0 | 67.3613 | 52.92% | C | 9.5895 | 3.4654 | 72.7587 | 71.8342 | 72.7069 | -3.7924 | -3.7945 | -4.4092 | 8.1257 | 7.8938 | 8.1171 | 39.9166 | 44.8968 | 41.9279 | 42.0833 | 43.7623 | 582598.37 | 683594.6772 | 182.7533 | 30.2061 | 29.8048 | 28.2206
33 | demand | 45 |  | yes | 7.2124 | 11.4439 | 3.9058 | 7.109 | 3H2 | 1.7575 | 5.2457 | 5.1189 | -2.477% | 2.9848 | 7.57 | 2.8287 | 7.9545 | 28.54% | 32.24% | 17.5% | 5.517% | -30.7% | 1400 | 0 | 77 | 67.6922 | 53.18% | C | 8.9409 | 2.5592 | 73.6332 | 72.958 | 73.719 | -4.8367 | -4.8902 | -5.5271 | 8.3772 | 8.0369 | 8.4513 | 39.9277 | 44.7136 | 42.3309 | 42.6025 | 43.8999 | 581822.3428 | 685146.0216 | 191.1465 | 28.9903 | 28.5769 | 27.4434
34 |  | 40 |  | yes | 5.9402 | 10.7027 | 2.074 | 5.8471 | 3H2 | 2.0363 | 5.483 | 5.3572 | -2.347% | 2.6924 | 7.352 | 2.5475 | 7.915 | 27.44% | 18.04% | 19.24% | 5.69% | -25.42% | 1400 | 75.1732 | 5.1133 | 63.7256 | 50.07% | C | 8.4156 | 1.1067 | 67.9132 | 69.1326 | 68.0323 | -6.9046 | -7.6501 | -7.7175 | 8.1892 | 8.2972 | 8.4707 | 34.9562 | 39.7379 | 36.7027 | 38.6935 | 38.1442 | 579056.8437 | 677812.6237 | 211.6961 | 26.926 | 26.5415 | 25.9001
35 |  | 35 |  | yes | 5.3645 | 10.5524 | 0.97833 | 5.3637 | 3H2 | 2.3633 | 5.7739 | 5.6799 | -1.655% | 2.4429 | 7.3902 | 2.2988 | 8.0006 | 24.42% | 14.04% | 17.32% | 6.266% | -21.87% | 1400 | 75.018 | 5.2694 | 56.6216 | 44.49% | B | 7.7395 | 0.042473 | 62.7217 | 64.001 | 63.2385 | -8.3112 | -9.0528 | -9.1141 | 8.2952 | 8.2756 | 8.6953 | 29.9968 | 34.8011 | 31.4622 | 33.6319 | 33.1 | 577583.7932 | 671182.5876 | 232.8706 | 25.8631 | 25.4842 | 24.7944
40 |  | 35 |  | yes | 7.6612 | 12.446 | 4.2567 | 7.2412 | 3H2 | 2.2955 | 5.7599 | 5.722 | -0.6616% | 2.5383 | 9.164 | 2.1805 | 8.1334 | 31.71% | 29.3% | 34.84% | 16.41% | -37.15% | 1400 | 76.1842 | 1.1267 | 70.09 | 55.07% | C | 10.2115 | 3.6443 | 61.9582 | 59.4938 | 59.3736 | -4.2878 | -4.3108 | -4.2653 | 8.8228 | 7.8003 | 8.8665 | 30.0132 | 34.7999 | 29.5164 | 31.1526 | 30.105 | 583262.4538 | 671136.2584 | 209.896 | 30.7797 | 30.3125 | 27.4416
47 |  | 35 |  | yes | 5.9105 | 11.0865 | 1.5663 | 5.6271 | 3H3 | 2.2428 | 5.6985 | 5.6294 | -1.226% | 2.5408 | 7.754 | 2.2735 | 8.0432 | 26.51% | 18.48% | 22.97% | 11.76% | -26.51% | 1401 | 75.5174 | 1.6693 | 71.09 | 155.1% | C | 8.8614 | 1.0754 | 63.4919 | 62.8386 | 62.2762 | -7.377 | -8.0157 | -8.1527 | 8.2008 | 8.2637 | 8.7855 | 30.0307 | 34.836 | 30.9351 | 33.052 | 32.5046 | 578520.5238 | 673233.505 | 223.6032 | 26.883 | 26.4888 | 25.4847
Note on W20: Author: still lower than select